## meta data
measurement_id | Name assigned to the data point
card | Data acquisition card number
physical_channel | Data acquisition channel address
channel_number | Channel number assigned to the data point
measurement_type | Type of measurement (e.g., flow, temperature, pressure)
signal_type | Nature of the data signal (AI - analog input; AO - analog output; DI - digital input; DO - digital output; RTD - resistance temperature detector; WD - watch dog)
subsystem | Subsystem the data point is associated with (e.g., AHU1, OAU)
instrument_m_n | Manufacturer number
instrument_s_n | Serial number
calibration_date | Calibration date
accuracy_scaled | Accuracy in engineering units or as percent of full scale
unit_raw | Raw units
unit_scaled | Scaled units
range_lo_raw | Lowest value of the data point in raw units
range_hi_raw | Largest value of the data point in raw units
startup | Value at startup
shutdown | Value at shutdown
scaling_coeff_a0 | Constant term of the polynomial function for converting from raw to scaled units
scaling_coeff_a1 | Linear term of the polynomial function for converting from raw to scaled units
scaling_coeff_a2 | Quadratic term of the polynomial function for converting from raw to scaled units

## sensors
time
ahu_dp | Differential pressure measurement in the secondary loop by the AHU coils
ahu1_cc_out_rtd | Temperature of the propylene glycol leaving the cooling coil in AHU1
ahu1_cc_rtd | Temperature of the air just after the cooling coil in AHU1
ahu1_f_cc | Flow rate of PG through the cooling coil in AHU1
ahu1_f_ra | Return airflow rate in AHU1
ahu1_f_sa | Supply airflow rate in AHU1
ahu1_fan_power | Power consumption of the AHU1 supply fan
ahu1_heat_c | Control signal for the electric heater in AHU1
ahu1_heat_power | Power consumption of the electric heater in AHU1
ahu1_heat_rtd | Temperature downstream of the electric heater in AHU1
ahu1_in_rtd | Temperature at the inlet of AHU1, after the return and supply air are mixed
ahu1_on | On/off control signal for the AHU1 supply fan
ahu1_out_rtd | Temperature downstream of AHU1
ahu1_p_down | Duct static pressure downstream of AHU1
ahu1_p_up | Static pressure upstream of the supply fan in AHU1
ahu1_rh_down | Relative humidity downstream of AHU1
ahu1_rh_ra | Relative humidity of the return air in AHU1
ahu1_rh_sa | Relative humidity of the supply air in AHU1
ahu1_rh_up | Relative humidity upstream of the supply fan in AHU1, after the return and supply air are mixed
ahu1_t_ra | Temperature of the return air in AHU1
ahu1_t_sa | Temperature of the supply air in AHU1
ahu1_tdb_ra | Dry bulb temperature of the return air in AHU1; same probe as ahu1_rh_ra
ahu1_tdb_sa | Dry bulb temperature of the supply air in AHU1; same probe as ahu1_rh_sa
ahu1_vfd | Speed of the AHU1 supply fan
ahu2_cc_out_rtd | Temperature of the propylene glycol leaving the cooling coil in AHU2
ahu2_cc_rtd | Temperature of the air just after the cooling coil in AHU2
ahu2_f_cc | Flow rate of PG through the cooling coil in AHU2
ahu2_f_ra | Return airflow rate in AHU2
ahu2_f_sa | Supply airflow rate in AHU2
ahu2_fan_power | Power consumption of the AHU2 supply fan
ahu2_heat_c | Control signal for the electric heater in AHU2
ahu2_heat_power | Power consumption of the electric heater in AHU2
ahu2_heat_rtd | Temperature downstream of the electric heater in AHU2
ahu2_in_rtd | Temperature at the inlet of AHU2, after the return and supply air are mixed
ahu2_on | On/off control signal for the AHU2 supply fan
ahu2_out_rtd | Temperature downstream of AHU2
ahu2_p_down | Duct static pressure downstream of AHU2
ahu2_p_up | Static pressure upstream of the supply fan in AHU2
ahu2_rh_down | Relative humidity downstream of AHU2
ahu2_rh_ra | Relative humidity of the return air in AHU2
ahu2_rh_up | Relative humidity upstream of the supply fan in AHU2, after the return and supply air are mixed
ahu2_t_ra | Temperature of the return air in AHU2
ahu2_t_sa | Temperature of the supply air in AHU2
ahu2_tdb_ra | Dry bulb temperature of the return air in AHU2; same probe as ahu2_rh_ra
ahu2_vfd | Speed of the AHU2 supply fan
ch1_c_out_rtd | Temperature of the water leaving the condenser in Chiller1
ch1_e_in_rtd | Temperature of the PG returning to both Chiller1 and Chiller2
ch1_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller1
ch1_f_c | Flow rate of the water through the condenser in Chiller1
ch1_f_e | Flow rate of the PG through the evaporator in Chiller1
ch1_on | On/off control signal for Chiller1
ch1_power | Power consumption of Chiller1
ch1_t_reset | Control to enable remote temperature setpoint for Chiller1
ch1_t_sp | Remote temperature setpoint for Chiller1
ch2_c_out_rtd | Temperature of the water leaving the condenser in Chiller2
ch2_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller2
ch2_f_c | Flow rate of the water through the condenser in Chiller2
ch2_f_e | Flow rate of the PG through the evaporator in Chiller2
ch2_on | On/off control signal for Chiller2
ch2_power | Power consumption of Chiller2
ch2_t_reset | Control to enable remote temperature setpoint for Chiller2
ch2_t_sp | Remote temperature setpoint for Chiller2
cl_f | Flow rate of water in the condensing loop
cw_in_rtd | Temperature of the chilled water entering the condensing loop
d10_pos_c | Control signal for the position of Damper10
d10_pos_fb | Feedback signal for the position of Damper10
d11_pos_c | Control signal for the position of Damper11
d11_pos_fb | Feedback signal for the position of Damper11
d15_pos_c | Control signal for the position of Damper15
d15_pos_fb | Feedback signal for the position of Damper15
d16_pos_c | Control signal for the position of Damper16
d16_pos_fb | Feedback signal for the position of Damper16
d17_pos_c | Control signal for the position of Damper17
d17_pos_fb | Feedback signal for the position of Damper17
d18_pos_c | Control signal for the position of Damper18
d18_pos_fb | Feedback signal for the position of Damper18
d2_pos_c | Control signal for the position of Damper2
d2_pos_fb | Feedback signal for the position of Damper2
d3_pos_c | Control signal for the position of Damper3
d3_pos_fb | Feedback signal for the position of Damper3
d4_pos_c | Control signal for the position of Damper4
d4_pos_fb | Feedback signal for the position of Damper4
d5_pos_c | Control signal for the position of Damper5
d5_pos_fb | Feedback signal for the position of Damper5
d6_pos_c | Control signal for the position of Damper6
d6_pos_fb | Feedback signal for the position of Damper6
d7_pos_c | Control signal for the position of Damper7
d7_pos_fb | Feedback signal for the position of Damper7
d8_pos_c | Control signal for the position of Damper8
d8_pos_fb | Feedback signal for the position of Damper8
dx_c1 | On/off signal for Compressor1 in the DX system
dx_c1_power | Partial measurement of power consumption of Compressor1 in the DX system
dx_c1_tsc1 | First temperature measurement used to estimate subcool in Compressor1 in the DX system
dx_c1_tsc2 | Second temperature measurement used to estimate subcool in Compressor1 in the DX system
dx_c1_tsh1 | First temperature measurement used to estimate superheat in Compressor1 in the DX system
dx_c1_tsh2 | Second temperature measurement used to estimate superheat in Compressor1 in the DX system
dx_c2 | On/off signal for Compressor2 in the DX system
dx_c2_power | Partial measurement of power consumption of Compressor2 in the DX system
dx_c2_tsc1 | First temperature measurement used to estimate subcool in Compressor2 in the DX system
dx_c2_tsc2 | Second temperature measurement used to estimate subcool in Compressor2 in the DX system
dx_c2_tsh1 | First temperature measurement used to estimate superheat in Compressor2 in the DX system
dx_c2_tsh2 | Second temperature measurement used to estimate superheat in Compressor2 in the DX system
dx_ds_c | Control signal for Compressor1 in the DX system
dx_m_cs | No longer used
dx_m_sclk | No longer used
dx_sp_cs | No longer used
dx_sp_din | No longer used
dx_sp_sclk | No longer used
dx_sp_spi | No longer used
dx_z_cs | No longer used
dx_z_din | No longer used
dx_z_sclk | No longer used
dx_z_spi | No longer used
exf1_f | Airflow rate at ExhaustFan1
exf1_on | On/off control for ExhaustFan1
exf1_p_down | Pressure downstream of ExhaustFan1
exf1_p_up | Pressure upstream of ExhaustFan1
exf1_power | Power consumption of ExhaustFan1
exf1_t_in | Temperature upstream of ExhaustFan1
exf1_vfd | Speed of ExhaustFan1
exf2_f | Airflow rate at ExhaustFan2
exf2_on | On/off control for ExhaustFan2
exf2_p_down | Pressure downstream of ExhaustFan2
exf2_p_up | Pressure upstream of ExhaustFan2
exf2_power | Power consumption of ExhaustFan2
exf2_t_in | Temperature upstream of ExhaustFan2
exf2_vfd | Speed of ExhaustFan2
hw_rtd | Temperature of the hot water entering the lab
hx1_f_hw | Flow rate of the hot water in HeatExchanger1
hx1_f_pg | Flow rate of the PG in HeatExchanger1
hx1_hw_rtd | Temperature of the hot water at the outlet of HeatExchanger1
hx1_pg_rtd | Tempeature of the PG at the outlet of HeatExchanger1
hx2_cw_rtd | Temperature of the chilled water at the outlet of HeatExchanger2
hx2_hw_rtd | Temperature of the hot water at the outlet of HeatExchanger2
hx3_cw_rtd | Temperature of the chilled water at the outlet of HeatExchanger3
hx3_f_cw | Flow rate of the chilled water through HeatExchanger3
hx3_f_pg | Flow rate of the PG through HeatExchanger3
hx3_pg_rtd | Temperature of the PG at the outlet of HeatExchanger3
indoor_p | Measurement of pressure in the IBAL
indoor_rh | Measurement of the relative humidity in the IBAL
indoor_rtd | Measurement of the temperature in the IBAL
mcc_run | On/off signal for the harmonic filter in the MCC
mcc_run_fb | Feedback for the on/off signal for the harmonic filter in the MCC
oau_cc_rtd | Air temperature downstream of the DX cooling coil in the OAU
oau_f_out | Airflow rate exhausting to the outdoors from the OAU
oau_fan_power | Power consumption of the OAU fan
oau_fz_in | Return signal from freezestat
oau_fz_out | Voltage signal to freezestat
oau_heat_c | Control signal for the electric heater in the OAU
oau_heat_power | Partial measurement of power consumption of the electric heater in the OAU
oau_hs_rtd | Temperature of the air just downstream of the electric heater in the OAU
oau_in_rtd | Temperatutre of the air at the inlet of the OAU, after the return and supply air mix
oau_on | On/off control signal for the OAU fan
oau_out_rtd | Temperature at the outlet of the OAU
oau_p_down | Static pressure downstream of the OAU fan
oau_p_up | Static pressure upstream of the OAU fan
oau_rh | Relative humidity at the outlet of the OAU
oau_t_out | Temperature of the air exhausting to the outdoors from the OAU
oau_vfd | Speed of the OAU fan
outdoor_rh | Relative humidity of the outdoor air
outdoor_rtd | Temperature of the outdoor air
pl_f | Flow rate in the primary loop
pl_ftemp | No longer used
pl_in_rtd | Temperautre of the PG entering (returning to) the primary loop
pl_out_rtd | Temperature of the PG leaving the primary loop
pump1_on | On/off control signal for Pump1
pump1_p_down | Pressure downstream of Pump1
pump1_p_up | Pressure upstream of Pump1
pump1_power | Power consumption of Pump1
pump1_vfd | Speed of Pump1
pump2_on | On/off control signal for Pump2
pump2_p_down | Pressure downstream of Pump2
pump2_p_up | Pressure upstream of Pump2
pump2_power | Power consumption of Pump2
pump2_vfd | Speed of Pump2
pump3_dp | Differential pressure across the secondary loop
pump3_on | On/off control signal for Pump3
pump3_out_rtd | Temperature downstream of Pump3
pump3_p_down | Pressure downstream of Pump3
pump3_p_up | Pressure upstream of Pump3
pump3_power | Power consumption of Pump3
pump3_vfd | Speed of Pump3
pump4_on | On/off control signal for Pump4
pump4_out_rtd | Temperature downstream of Pump4
pump4_p_down | Pressure downstream of Pump4
pump4_p_up | Pressure upstream of Pump4
pump4_power | Power consumption of Pump4
pump4_vfd | Speed of Pump4
pump5_on | On/off control signal for Pump5
pump5_p_down | Pressure downstream of Pump5
pump5_p_up | Pressure upstream of Pump5
pump5_power | Power consumption of Pump5
pump5_vfd | Speed of Pump5
sl_f | Flow rate in the secondary loop
sl_ftemp | No longer used
sl_out_rtd | Temperature at the outlet of the secondary loop
timer | No longer used
tmc1_in_rtd | Temperature of the water entering the Thermal Mass Coil 1
tmc1_out_rtd | Temperature of the water leaving Thermal Mass Coil 1
tmc1_pos_c | Position of the throttling valve in Thermal Mass Coil 1
tmc1_pump_on | On/off control signal for the pump in Thermal Mass Coil 1
tmc2_in_rtd | Temperature of the water entering the Thermal Mass Coil 2
tmc2_out_rtd | Temperature of the water leaving Thermal Mass Coil 2
tmc2_pos_c | Position of the throttling valve in Thermal Mass Coil 2
tmc2_pump_on | On/off control signal for the pump in Thermal Mass Coil 2
tmc3_in_rtd | Temperature of the water entering the Thermal Mass Coil 3
tmc3_out_rtd | Temperature of the water leaving Thermal Mass Coil 3
tmc3_pos_c | Position of the throttling valve in Thermal Mass Coil 3
tmc3_pump_on | On/off control signal for the pump in Thermal Mass Coil 3
tmc4_in_rtd | Temperature of the water entering the Thermal Mass Coil 4
tmc4_out_rtd | Temperature of the water leaving Thermal Mass Coil 4
tmc4_pos_c | Position of the throttling valve in Thermal Mass Coil 4
tmc4_pump_on | On/off control signal for the pump in Thermal Mass Coil 4
ts_f | Flow rate through the thermal storage tank
ts_in_rtd | Temperature of the PG entering the thermal storage tank
ts_meter | Ice meter reading of the inventory in the thermal storage tank
ts_out_rtd | Temperature of the PG leaving the thermal storage tank
v1_pos_c | Control signal for the position of Valve1
v1_pos_fb | Feedback signal for the position of Valve1
v10_pos_c | Control signal for the position of Valve10
v10_pos_fb | Feedback signal for the position of Valve10
v11_pos_c | Control signal for the position of Valve11
v11_pos_fb | Feedback signal for the position of Valve11
v12_pos_c | Control signal for the position of Valve12
v12_pos_fb | Feedback signal for the position of Valve12
v13_pos_c | Control signal for the position of Valve13
v13_pos_fb | Feedback signal for the position of Valve13
v14_pos_c | Control signal for the position of Valve14
v14_pos_fb | Feedback signal for the position of Valve14
v15_pos_c | Control signal for the position of Valve15
v15_pos_fb | Feedback signal for the position of Valve15
v16_pos_c | Control signal for the position of Valve16
v16_pos_fb | Feedback signal for the position of Valve16
v17_pos_c | Control signal for the position of Valve17
v17_pos_fb | Feedback signal for the position of Valve17
v18_pos_c | Control signal for the position of Valve18
v18_pos_fb | Feedback signal for the position of Valve18
v19_pos_c | Control signal for the position of Valve19
v19_pos_fb | Feedback signal for the position of Valve19
v2_pos_c | Control signal for the position of Valve2
v2_pos_fb | Feedback signal for the position of Valve2
v20_pos_c | Control signal for the position of Valve20
v20_pos_fb | Feedback signal for the position of Valve20
v3_pos_c | Control signal for the position of Valve3
v3_pos_fb | Feedback signal for the position of Valve3
v4_pos_c | Control signal for the position of Valve4
v4_pos_fb | Feedback signal for the position of Valve4
v5_pos_c | Control signal for the position of Valve5
v5_pos_fb | Feedback signal for the position of Valve5
v6_pos_c | Control signal for the position of Valve6
v6_pos_fb | Feedback signal for the position of Valve6
v7_pos_c | Control signal for the position of Valve7
v7_pos_fb | Feedback signal for the position of Valve7
v8_pos_c | Control signal for the position of Valve8
v8_pos_fb | Feedback signal for the position of Valve8
v9_pos_c | Control signal for the position of Valve9
v9_pos_fb | Feedback signal for the position of Valve9
vav1_f | Airflow rate through VAV1
vav1_heat_c | Control signal for the electric reheat in VAV1
vav1_heat_power | Power consumption of the electric reheat in VAV1
vav1_out_rtd | Temperature of the air downstream of VAV1
vav1_t_in | Temperature of the air upstream of VAV1
vav2_f | Airflow rate through VAV2
vav2_heat_c | Control signal for the electric reheat in VAV2
vav2_heat_power | Power consumption of the electric reheat in VAV2
vav2_out_rtd | Temperature of the air downstream of VAV2
vav2_t_in | Temperature of the air upstream of VAV2
vav3_f | Airflow rate through VAV3
vav3_heat_c | Control signal for the electric reheat in VAV3
vav3_heat_power | Power consumption of the electric reheat in VAV3
vav3_out_rtd | Temperature of the air downstream of VAV3
vav3_t_in | Temperature of the air upstream of VAV3
vav4_f | Airflow rate through VAV4
vav4_heat_c | Control signal for the electric reheat in VAV4
vav4_heat_power | Power consumption of the electric reheat in VAV4
vav4_out_rtd | Temperature of the air downstream of VAV4
vav4_t_in | Temperature of the air upstream of VAV4
vch1_pos_fb | No longer used
vch2_pos_fb | No longer used
vsh_in | Return signal for the shutoff valves for the chilled and hot water
vsh_out | Control signal for the shutoff valves for the chilled and hot water
zs1_heat_c | Control signal for the electric heater in ZS1
zs1_heat_power | Power consumption of the electric heater in ZS1
zs1_heat_rtd | Temperature of the air downstream of the electric heater in ZS1
zs1_out_rtd | Temperature of the air downstream of ZS1 (zone temperature)
zs1_rh | Relative humidity of the air downstream of ZS1 (zone relative humidity)
zs2_heat_c | Control signal for the electric heater in ZS2
zs2_heat_power | Power consumption of the electric heater in ZS2
zs2_heat_rtd | Temperature of the air downstream of the electric heater in ZS2
zs2_out_rtd | Temperature of the air downstream of ZS2 (zone temperature)
zs2_rh | Relative humidity of the air downstream of ZS2 (zone relative humidity)
zs3_heat_c | Control signal for the electric heater in ZS3
zs3_heat_power | Power consumption of the electric heater in ZS3
zs3_heat_rtd | Temperature of the air downstream of the electric heater in ZS3
zs3_out_rtd | Temperature of the air downstream of ZS3 (zone temperature)
zs3_rh | Relative humidity of the air downstream of ZS3 (zone relative humidity)
zs4_heat_c | Control signal for the electric heater in ZS4
zs4_heat_power | Power consumption of the electric heater in ZS4
zs4_heat_rtd | Temperature of the air downstream of the electric heater in ZS4
zs4_out_rtd | Temperature of the air downstream of ZS4 (zone temperature)
zs4_rh | Relative humidity of the air downstream of ZS4 (zone relative humidity)
cl_t_sp_f | Temperature setpoint of the water in the condensing loop
cl_t_kp | Proportional gain for the PI controller for the temperature of the condensing loop
cl_t_ki | Integral gain for the PI controller for the temperature of the condensing loop
cl_t_kd | Derivative gain for the PI controller for the temperature of the condensing loop
cl_t_ubias | Bias term for the PI controller for the temperature of the condensing loop
cl_t_sp_high | Upper limit on the temperature setpoint in the condensing loop
cl_t_sp_low | Lower limit on the temperature setpoint in the condensing loop
cl_t_pv_f | Actual temperature being controlled in the condensing loop
cl_t_cv_v | Control signal for Valve3, the control valve, in the condensing loop
cl_t_error_f | Difference between the actual and setpoint temperatures in the condensing loop
cl_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures in the condensing loop
cl_t_prop_term | Proportional term in the PI controller for the condensing loop
cl_t_int_term | Integral term in the PI controller for the condensing loop
sl_t_sp_f | Temperature setpoint of the PG in the secondary loop
sl_t_kp | Proportional gain for the PI controller for the temperature of the secondary loop
sl_t_ki | Integral gain for the PI controller for the temperature of the secondary loop
sl_t_kd | Derivative gain for the PI controller for the temperature of the secondary loop
sl_t_ubias | Bias term for the PI controller for the temperature of the secondary loop
sl_t_sp_high | Upper limit on the temperature setpoint in the secondary loop
sl_t_sp_low | Lower limit on the temperature setpoint in the secondary loop
sl_t_pv_f | Actual temperature being controlled in the secondary loop
sl_t_cv_v | Control signal for Valve9, the control valve, in the secondary loop
sl_t_error_f | Difference between the actual and setpoint temperatures in the secondary loop
sl_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures in the secondary loop
sl_DB | No longer used
sl_vfd_sp_v | Pump speed setpoint for the secondary loop pump
sl_vfd_kp | Proportional gain for the PI controller for the pump speed in the secondary loop
sl_vfd_ki | Integral gain for the PI controller for the pump speed in the secondary loop
sl_vfd_kd | Derivative gain for the PI controller for the pump speed in the secondary loop
sl_vfd_ubias | Bias for the PI controller for the pump speed in the secondary loop
sl_vfd_sp_high | Upper limit on the pump speed in the secondary loop
sl_vfd_sp_low | Lower limit on the pump speed in the secondary loop
sl_vfd_pv_v | Actual pump speed being controlled in the secondary loop
sl_vfd_cv_hz | Control signal for Pump3, the secondary loop pump
sl_vfd_error_v | Difference between the actual and setpoint pump speeds in the secondary loop
sl_vfd_cum_error_v | Integral error term - sum of the difference between the actual and setpoint pump speeds in the secondary loop
sl_n_pr | Number of timesteps between setpoint changes for pressure reset in the secondary loop
sl_thresh_low_pr | Threshold on the cooling coil valves that indicates less cooling is needed (the positions of both valves are below this threshold)
sl_thresh_high_pr | Threshold on the cooling coil valves that indicates more cooling is needed (the position of at least one valve exceeds this threshold)
sl_delta_pr | Magnitude of the change of the pressure setpoint in the secondary loop
ts_end_charging | Flag to indicate that charging of the thermal storage tank is complete
ts_t_sp_f | Temperature setpoint of the PG leaving the thermal storage tank
ts_t_kp | Proportional gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_ki | Integral gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_kd | Derivative gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_ubias | Bias term for the PI controller for the temperature leaving the thermal storage tank
ts_t_sp_high | Upper limit on the temperature setpoint of the PG leaving the thermal storage tank
ts_t_sp_low | Lower limit on the temperature setpoint of the PG leaving the thermal storage tank
ts_t_pv_f | Actual temperature being controlled after the thermal storage tank
ts_t_cv_v | Control signal for Valve8, the control valve, for the PG leaving the thermal storage tank
ts_t_error_f | Difference between the actual and setpoint temperatures leaving the thermal storage tank
ts_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures leaving the thermal storage tank
hx1_t_sp_f | Temperature setpoint of the PG leaving HX1
hx1_t_kp | Proportional gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_ki | Integral gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_kd | Derivative gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_ubias | Bias term for the PI controller for the temperature of the PG leaving HX1
hx1_t_sp_high | Upper limit on the temperature setpoint of the PG leaving HX1
hx1_t_sp_low | Lower limit on the temperature setpoint of the PG leaving HX1
hx1_t_pv_f | Actual temperature of the PG being controlled in HX1
hx1_t_dt_f | No longer used
hx1_t_error_f | Difference between the actual and setpoint temperatures of the PG leaving HX1
hx1_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures of the PG leaving HX1
hx1_t_cv_v | Control signal for Valve10, the control valve, in the PG side of HX1
hx1_load_sp_kw | Load setpoint for HX1
hx1_load_pv_inst_kw | Actual load generated by HX1
hx1_load_kp | Proportional gain for the PI controller for the load generated by HX1
hx1_load_ki | Integral gain for the PI controller for the load generated by HX1
hx1_load_kd | Derivative gain for the PI controller for the load generated by HX1
hx1_load_ubias | Bias term for the PI controller for the load generated by HX1
hx1_load_sp_high | Upper limit on the load setpoint in HX1
hx1_load_sp_low | Lower limit on the load setpoint in HX1
hx1_load_pv_avg_kw | Averaged actual load generated by HX1
hx1_load_cv_v | Control signal for Valve11, the control valve, in HX1
hx1_load_dq_kw | No longer used
hx1_load_error_kw | Difference between the actual and setpoint loads in HX1
hx1_load_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint loads in HX1
ch1_t_sp_f | Temperature setpoint for Chiller1
ch2_t_sp_f | Temperature setpoint for Chiller2
oau_h_t_sp_f | Temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_kp | Proportional gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_ki | Integral gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_kd | Derivative gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_ubias | Bias term for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_sp_high | Upper limit on the temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_sp_low | Lower limit on the temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_pv_f | Actual temperature of the air leaving the heating coil in the OAU
oau_h_t_cv_v | Control signal for the OAU heater
oau_h_t_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in the OAU
oau_h_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in the OAU
oau_h_prop_term | Proportional term in the PI controller for the heating coil in the OAU
oau_h_int_term | Integral term in the PI controller for the heating coil in the OAU
oau_h_threshold | No longer used
oau_h_delay | No longer used
oau_h_dtheat | No longer used
oau_h_outdoor_rtd_mean | No longer used
oau_c_t_kd | Derivative gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_kp | Proportional gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_ki | Integral gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_ubias | Bias term for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_sp_high | Upper limit on the humidity ratio leaving the OAU
oau_c_t_sp_low | Lower limit on the humidity ratio leaving the OAU
oau_c_t_sp_f | Setpoint humidity ratio of the air leaving the OAU
oau_c_t_pv_f | Actual humidity ratio of the air leaving the OAU
oau_c_t_cum_error_f | Integral error term - difference between the actual and setpoint humidity ratios of the air leaving the OAU
oau_c_prop_term | Proportional term in the PI controller for the heating coil in the OAU
oau_c_int_term | Integral term in the PI controller for the heating coil in the OAU
oau_c_delay | No longer used
oau_c_t_cv_v | Control signal for Compressor1 in the cooling coil in the OAU
oau_c_t_error_f | Difference between the actual and setpoint humidity ratios of the air leaving the OAU
oau_c_dt | no longer used
oau_c_delay2 | no longer used
oau_w_rh_sp_per | Setpoint relative humidity of the air leaving the OAU
oau_w_rh_kp | Proportional gain for the humidifier PI controller in the OAU
oau_w_rh_ki | Integral gain for the humidifier PI controller in the OAU
oau_w_rh_kd | Derivative gain for the humidifier PI controller in the OAU
oau_w_rh_ubias | Bias term for the humidifier PI controller in the OAU
oau_w_rh_sp_high | Upper limit on the relative humidity leaving the OAU
oau_w_rh_sp_low | Lower limit on the relative humidity leaving the OAU
oau_w_rh_pv_per | Actual relative humidity leaving the OAU
oau_w_rh_cv_v | Control signal for Valve2, the control valve for the humidifier
oau_w_rh_error_per | Difference between the actual and setpoint relative humidity of the air leaving the OAU
oau_w_rh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint relative humidity of the air leaving the OAU
oau_w_prop_term | Proportional term in the PI controller for the humidifier in the OAU
oau_w_int_term | Integral term in the PI controller for the humidifier in the OAU
oau_t_out_sp_f | Setpoint temperature of the air leaving the OAU
oau_rh_out_sp_per | Setpoint relative humidity of the air leaving the OAU
oau_read_from_file | Flag to indicate that the OAU setpoints should be read from file
bc_n_sl_on | Number of timesteps that the secondary loop pump has to be on for there to be a building load
bc_n_q_mean | Number of timesteps to include in the calculation of the average load
bc_n_chiller_fault | Number of chiller fault flags before a chiller is considered to be in a fault status
bc_n_pump3_max | No longer used
bc_n_stage_up | Number of timesteps in the current stage before a chiller can be staged up
bc_n_stage_down | Number of timesteps in the current stage before a chiller can be staged down
bc_q1_min | Minimum load that allows Chiller1 to be enabled
bc_q1_sd | Load at which Chiller1 is staged down (turned off)
bc_q1_su | No longer used
bc_q2_min | Minimum load that allows Chiller2 to be enabled
bc_q2_sd | Load at which Chiller2 is staged down (turned off)
bc_q2_su | No longer used
bc_q3_min | No longer used
bc_q3_sd | No longer used
bc_q3_su | No longer used
bc_v10_sp | No longer used
bc_dt_sl | Value by which to offset the chiller setpoint temperature for the secondary loop
bc_max_plant_load_kw | No longer used
bc_pump3_max_vfd | No longer used
bc_n_trans | Number of timesteps for transition between stages
bc_n_viol | Number of timesteps that a violation has to occur before the stage can change
stage_up_down_count | Number of timesteps when a stage up or down is requested
stage_stage | The current stage that the chillers are in
stage_allow_stage_up_time | Flag to indicate that a chiller can stage up
stage_allow_stage_down_time | Flag to indicate that a chiller can stage down
stage_allow_stage_up_pump3 | No longer used
stage_allow_stage_down_temp | No longer used
zs1_qs_sp_kw | Sensible load setpoint for ZS1
zs1_qs_pv_kw | Actual sensible load in ZS1
zs1_qs_ca_a | Control signal for the heating coil in ZS1
zs1_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS1
zs1_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS1
zs1_ql_sp_kw | Latent load setpoint for ZS1
zs1_ql_pv_kw | Actual latent load in ZS1
zs1_ql_cv_v | Control signal for Valve14, the control valve for the humidifier in ZS1
zs1_ql_error_kw | Difference between the actual and setpoint latent loads in ZS1
zs1_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS1
zs1_qs_kp | Proportional gain for the PI controller for the sensible load in ZS1
zs1_qs_ki | Integral gain for the PI controller for the sensible load in ZS1
zs1_qs_kd | Derivative gain for the PI controller for the sensible load in ZS1
zs1_qs_ubias | Bias term for the PI controller for the sensible load in ZS1
zs1_qs_sp_hi | Upper limit on the sensible load setpoint in ZS1
zs1_qs_sp_low | Lower limit on the sensible load setpoint in ZS1
zs1_ql_kp | Proportional gain for the PI controller for the latent load in ZS1
zs1_ql_ki | Integral gain for the PI controller for the latent load in ZS1
zs1_ql_kd | Derivative gain for the PI controller for the latent load in ZS1
zs1_ql_ubias | Bias term for the PI controller for the latent load in ZS1
zs1_ql_sp_hi | Upper limit on the latent load setpoint in ZS1
zs1_ql_sp_low | Lower limit on the latent load setpoint in ZS1
zs1_t_sp_f | Setpoint temperature for the air leaving ZS1
zs1_rh_sp_per | Relative humidity setpoint for the air leaving ZS1
zs2_qs_sp_kw | Sensible load setpoint for ZS2
zs2_qs_pv_kw | Actual sensible load in ZS2
zs2_qs_ca_a | Control signal for the heating coil in ZS2
zs2_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS2
zs2_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS2
zs2_ql_sp_kw | Latent load setpoint for ZS2
zs2_ql_pv_kw | Actual latent load in ZS2
zs2_ql_cv_v | Control signal for Valve15, the control valve for the humidifier in ZS2
zs2_ql_error_kw | Difference between the actual and setpoint latent loads in ZS2
zs2_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS2
zs2_qs_kp | Proportional gain for the PI controller for the sensible load in ZS2
zs2_qs_ki | Integral gain for the PI controller for the sensible load in ZS2
zs2_qs_kd | Derivative gain for the PI controller for the sensible load in ZS2
zs2_qs_ubias | Bias term for the PI controller for the sensible load in ZS2
zs2_qs_sp_hi | Upper limit on the sensible load setpoint in ZS2
zs2_qs_sp_low | Lower limit on the sensible load setpoint in ZS2
zs2_ql_kp | Proportional gain for the PI controller for the latent load in ZS2
zs2_ql_ki | Integral gain for the PI controller for the latent load in ZS2
zs2_ql_kd | Derivative gain for the PI controller for the latent load in ZS2
zs2_ql_ubias | Bias term for the PI controller for the latent load in ZS2
zs2_ql_sp_hi | Upper limit on the latent load setpoint in ZS2
zs2_ql_sp_low | Lower limit on the latent load setpoint in ZS2
zs2_rh_sp_per | Setpoint temperature for the air leaving ZS2
zs2_t_sp_f | Relative humidity setpoint for the air leaving ZS2
zs3_qs_sp_kw | Sensible load setpoint for ZS3
zs3_qs_pv_kw | Actual sensible load in ZS3
zs3_qs_ca_a | Control signal for the heating coil in ZS3
zs3_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS3
zs3_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS3
zs3_ql_sp_kw | Latent load setpoint for ZS3
zs3_ql_pv_kw | Actual latent load in ZS3
zs3_ql_cv_v | Control signal for Valve16, the control valve for the humidifier in ZS3
zs3_ql_error_kw | Difference between the actual and setpoint latent loads in ZS3
zs3_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS3
zs3_qs_kp | Proportional gain for the PI controller for the sensible load in ZS3
zs3_qs_ki | Integral gain for the PI controller for the sensible load in ZS3
zs3_qs_kd | Derivative gain for the PI controller for the sensible load in ZS3
zs3_qs_ubias | Bias term for the PI controller for the sensible load in ZS3
zs3_qs_sp_hi | Upper limit on the sensible load setpoint in ZS3
zs3_qs_sp_low | Lower limit on the sensible load setpoint in ZS3
zs3_ql_kp | Proportional gain for the PI controller for the latent load in ZS3
zs3_ql_ki | Integral gain for the PI controller for the latent load in ZS3
zs3_ql_kd | Derivative gain for the PI controller for the latent load in ZS3
zs3_ql_ubias | Bias term for the PI controller for the latent load in ZS3
zs3_ql_sp_hi | Upper limit on the latent load setpoint in ZS3
zs3_ql_sp_low | Lower limit on the latent load setpoint in ZS3
zs3_rh_sp_per | Setpoint temperature for the air leaving ZS3
zs3_t_sp_f | Relative humidity setpoint for the air leaving ZS3
zs4_qs_sp_kw | Sensible load setpoint for ZS4
zs4_qs_pv_kw | Actual sensible load in ZS4
zs4_qs_ca_a | Control signal for the heating coil in ZS4
zs4_qs_error_kw | Difference between the actual and setpoint sensible loads in ZS4
zs4_qs_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS4
zs4_ql_sp_kw | Latent load setpoint for ZS4
zs4_ql_pv_kw | Actual latent load in ZS4
zs4_ql_cv_v | Control signal for Valve17, the control valve for the humidifier in ZS4
zs4_ql_error_kw | Difference between the actual and setpoint latent loads in ZS4
zs4_ql_cum_error_kw | Integral error - sum of the difference between the actual and setpoint latent loads in ZS4
zs4_qs_kp | Proportional gain for the PI controller for the sensible load in ZS4
zs4_qs_ki | Integral gain for the PI controller for the sensible load in ZS4
zs4_qs_kd | Derivative gain for the PI controller for the sensible load in ZS4
zs4_qs_ubias | Bias term for the PI controller for the sensible load in ZS4
zs4_qs_sp_hi | Upper limit on the sensible load setpoint in ZS4
zs4_qs_sp_low | Lower limit on the sensible load setpoint in ZS4
zs4_ql_kp | Proportional gain for the PI controller for the latent load in ZS4
zs4_ql_ki | Integral gain for the PI controller for the latent load in ZS4
zs4_ql_kd | Derivative gain for the PI controller for the latent load in ZS4
zs4_ql_ubias | Bias term for the PI controller for the latent load in ZS4
zs4_ql_sp_hi | Upper limit on the latent load setpoint in ZS4
zs4_ql_sp_low | Lower limit on the latent load setpoint in ZS4
zs4_rh_sp_per | Setpoint temperature for the air leaving ZS4
zs4_t_sp_f | Relative humidity setpoint for the air leaving ZS4
ahu1_h_sp_f | Setpoint temperature for the air leaving the heating coil in AHU1
ahu1_h_kp | Proportional gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_ki | Integral gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_kd | Derivative gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_ubias | Bias term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_sp_high | Upper limit on the temperature setpoint for the heating coil in AHU1
ahu1_h_sp_low | Lower limit on the temperature setpoint for the heating coil in AHU1
ahu1_h_pv_f | Actual temperature of the air leaving the heating coil in AHU1
ahu1_h_cv_v | Control signal for the heating coil in AHU1
ahu1_h_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU1
ahu1_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU1
ahu1_h_prop_term | Proportional term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_int_term | Integral term for the PI controller for the air leaving the heating coil in AHU1
ahu1_cc_sp_f | Setpoint temperature for the air leaving the cooling coil in AHU1
ahu1_cc_kp | Proportional gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_ki | Integral gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_kd | Derivative gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_ubias | Bias term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_sp_high | Upper limit on the temperature setpoint for the cooling coil in AHU1
ahu1_cc_sp_low | Lower limit on the temperature setpoint for the cooling coil in AHU1
ahu1_cc_pv_f | Actual temperature of the air leaving the cooling coil in AHU1
ahu1_cc_cv_v | Control signal for the cooling coil in AHU1
ahu1_cc_error_f | Difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU1
ahu1_cc_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU1
ahu1_cc_prop_term | Proportional term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_int_term | Integral term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_fan_sp_inh2o | Pressure setpoint for the supply fan in AHU1
ahu1_fan_kp | Proportional gain for the PI controller for the supply fan in AHU1
ahu1_fan_ki | Integral gain for the PI controller for the supply fan in AHU1
ahu1_fan_kd | Derivative gain for the PI controller for the supply fan in AHU1
ahu1_fan_ubias | Bias term for the PI controller for the supply fan in AHU1
ahu1_fan_sp_high | Upper limit on the pressure setpoint for the supply fan in AHU1
ahu1_fan_sp_low | Lower limit on the pressure setpoint for the supply fan in AHU1
ahu1_fan_pv_inh2o | Actual static pressure downstream of AHU1
ahu1_fan_cv_hz | Control signal for the speed of the supply fan in AHU1
ahu1_fan_error_inh2o | Difference between the actual and setpoint pressures downstream of AHU1
ahu1_fan_cum_error_inh2o | Integral error - sum of the difference between the actual and setpoint pressures downstream of AHU1
ahu1_fan_prop_term | Proportional term for the PI controller for the speed of the supply fan in AHU1
ahu1_fan_int_term | Integral term for the PI controller for the speed of the supply fan in AHU1
ahu2_h_sp_f | Setpoint temperature for the air leaving the heating coil in AHU2
ahu2_h_kp | Proportional gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_ki | Integral gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_kd | Derivative gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_ubias | Bias term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_sp_high | Upper limit on the temperature setpoint for the heating coil in AHU2
ahu2_h_sp_low | Lower limit on the temperature setpoint for the heating coil in AHU2
ahu2_h_pv_f | Actual temperature of the air leaving the heating coil in AHU2
ahu2_h_cv_v | Control signal for the heating coil in AHU2
ahu2_h_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU2
ahu2_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU2
ahu2_h_prop_term | Proportional term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_int_term | Integral term for the PI controller for the air leaving the heating coil in AHU2
ahu2_cc_sp_f | Setpoint temperature for the air leaving the cooling coil in AHU2
ahu2_cc_kp | Proportional gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_ki | Integral gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_kd | Derivative gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_ubias | Bias term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_sp_high | Upper limit on the temperature setpoint for the cooling coil in AHU2
ahu2_cc_sp_low | Lower limit on the temperature setpoint for the cooling coil in AHU2
ahu2_cc_pv_f | Actual temperature of the air leaving the cooling coil in AHU2
ahu2_cc_cv_v | Control signal for the cooling coil in AHU2
ahu2_cc_error_f | Difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU2
ahu2_cc_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU2
ahu2_cc_prop_term | Proportional term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_int_term | Integral term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_fan_sp_inh2o | Pressure setpoint for the supply fan in AHU2
ahu2_fan_kp | Proportional gain for the PI controller for the supply fan in AHU2
ahu2_fan_ki | Integral gain for the PI controller for the supply fan in AHU2
ahu2_fan_kd | Derivative gain for the PI controller for the supply fan in AHU2
ahu2_fan_ubias | Bias term for the PI controller for the supply fan in AHU2
ahu2_fan_sp_high | Upper limit on the pressure setpoint for the supply fan in AHU2
ahu2_fan_sp_low | Lower limit on the pressure setpoint for the supply fan in AHU2
ahu2_fan_pv_inh2o | Actual static pressure downstream of AHU2
ahu2_fan_cv_hz | Control signal for the speed of the supply fan in AHU2
ahu2_fan_error_inh2o | Difference between the actual and setpoint pressures downstream of AHU2
ahu2_fan_cum_error_inh2o | Integral error - sum of the difference between the actual and setpoint pressures downstream of AHU2
ahu2_fan_prop_term | Proportional term for the PI controller for the speed of the supply fan in AHU2
ahu2_fan_int_term | Integral term for the PI controller for the speed of the supply fan in AHU2
vav1_d_sp | Flow setpont for the PI controller for the damper in VAV1
vav1_d_kp | Proportional gain for the PI controller for the damper in VAV1
vav1_d_ki | Integral gain for the PI controller for the damper in VAV1
vav1_d_kd | Derivative gain for the PI controller for the damper in VAV1
vav1_d_ubias | Bias term for the PI controller for the damper in VAV1
vav1_d_sp_high | Upper limit on the flow setpoint for VAV1
vav1_d_sp_low | Lower limit on the flow setpoint for VAV1
vav1_d_pv | Actual airflow rate in VAV1
vav1_d_cv_output | Control signal for Damper15, the control damper, in VAV1
vav1_d_error | Difference between the actual and setpoint flows in VAV1
vav1_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV1
vav1_d_prop_term | Proportional term for the PI controller for the damper in VAV1
vav1_d_int_term | Integral term for the PI controller for the damper in VAV1
vav1_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV1
vav1_h_kp | Proportional gain for the PI controller for the heating coil in VAV1
vav1_h_ki | Integral gain for the PI controller for the heating coil in VAV1
vav1_h_kd | Derivative gain for the PI controller for the heating coil in VAV1
vav1_h_ubias | Bias term for the PI controller for the heating coil in VAV1
vav1_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV1
vav1_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV1
vav1_h_pv_f | Actual temperature of the air after the heating coil in VAV1
vav1_h_cv_v | Control signal for the heating coil in VAV1
vav1_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV1
vav1_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV1
vav1_h_prop_term | Proportional term for the PI controller for the heating coil in VAV1
vav1_h_int_term | Integral term for the PI controller for the heating coil in VAV1
vav2_d_sp | Flow setpont for the PI controller for the damper in VAV2
vav2_d_kp | Proportional gain for the PI controller for the damper in VAV2
vav2_d_ki | Integral gain for the PI controller for the damper in VAV2
vav2_d_kd | Derivative gain for the PI controller for the damper in VAV2
vav2_d_ubias | Bias term for the PI controller for the damper in VAV2
vav2_d_sp_high | Upper limit on the flow setpoint for VAV2
vav2_d_sp_low | Lower limit on the flow setpoint for VAV2
vav2_d_pv | Actual airflow rate in VAV2
vav2_d_cv_output | Control signal for Damper16, the control damper, in VAV2
vav2_d_error | Difference between the actual and setpoint flows in VAV2
vav2_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV2
vav2_d_prop_term | Proportional term for the PI controller for the damper in VAV2
vav2_d_int_term | Integral term for the PI controller for the damper in VAV2
vav2_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV2
vav2_h_kp | Proportional gain for the PI controller for the heating coil in VAV2
vav2_h_ki | Integral gain for the PI controller for the heating coil in VAV2
vav2_h_kd | Derivative gain for the PI controller for the heating coil in VAV2
vav2_h_ubias | Bias term for the PI controller for the heating coil in VAV2
vav2_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV2
vav2_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV2
vav2_h_pv_f | Actual temperature of the air after the heating coil in VAV2
vav2_h_cv_v | Control signal for the heating coil in VAV2
vav2_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV2
vav2_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV2
vav2_h_prop_term | Proportional term for the PI controller for the heating coil in VAV2
vav2_h_int_term | Integral term for the PI controller for the heating coil in VAV2
vav3_d_sp | Flow setpont for the PI controller for the damper in VAV3
vav3_d_kp | Proportional gain for the PI controller for the damper in VAV3
vav3_d_ki | Integral gain for the PI controller for the damper in VAV3
vav3_d_kd | Derivative gain for the PI controller for the damper in VAV3
vav3_d_ubias | Bias term for the PI controller for the damper in VAV3
vav3_d_sp_high | Upper limit on the flow setpoint for VAV3
vav3_d_sp_low | Lower limit on the flow setpoint for VAV3
vav3_d_pv | Actual airflow rate in VAV3
vav3_d_cv_output | Control signal for Damper17, the control damper, in VAV3
vav3_d_error | Difference between the actual and setpoint flows in VAV3
vav3_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV3
vav3_d_prop_term | Proportional term for the PI controller for the damper in VAV3
vav3_d_int_term | Integral term for the PI controller for the damper in VAV3
vav3_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV3
vav3_h_kp | Proportional gain for the PI controller for the heating coil in VAV3
vav3_h_ki | Integral gain for the PI controller for the heating coil in VAV3
vav3_h_kd | Derivative gain for the PI controller for the heating coil in VAV3
vav3_h_ubias | Bias term for the PI controller for the heating coil in VAV3
vav3_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV3
vav3_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV3
vav3_h_pv_f | Actual temperature of the air after the heating coil in VAV3
vav3_h_cv_v | Control signal for the heating coil in VAV3
vav3_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV3
vav3_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV3
vav3_h_prop_term | Proportional term for the PI controller for the heating coil in VAV3
vav3_h_int_term | Integral term for the PI controller for the heating coil in VAV3
vav4_d_sp | Flow setpont for the PI controller for the damper in VAV4
vav4_d_kp | Proportional gain for the PI controller for the damper in VAV4
vav4_d_ki | Integral gain for the PI controller for the damper in VAV4
vav4_d_kd | Derivative gain for the PI controller for the damper in VAV4
vav4_d_ubias | Bias term for the PI controller for the damper in VAV4
vav4_d_sp_high | Upper limit on the flow setpoint for VAV4
vav4_d_sp_low | Lower limit on the flow setpoint for VAV4
vav4_d_pv | Actual airflow rate in VAV4
vav4_d_cv_output | Control signal for Damper18, the control damper, in VAV4
vav4_d_error | Difference between the actual and setpoint flows in VAV4
vav4_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV4
vav4_d_prop_term | Proportional term for the PI controller for the damper in VAV4
vav4_d_int_term | Integral term for the PI controller for the damper in VAV4
vav4_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV4
vav4_h_kp | Proportional gain for the PI controller for the heating coil in VAV4
vav4_h_ki | Integral gain for the PI controller for the heating coil in VAV4
vav4_h_kd | Derivative gain for the PI controller for the heating coil in VAV4
vav4_h_ubias | Bias term for the PI controller for the heating coil in VAV4
vav4_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV4
vav4_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV4
vav4_h_pv_f | Actual temperature of the air after the heating coil in VAV4
vav4_h_cv_v | Control signal for the heating coil in VAV4
vav4_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV4
vav4_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV4
vav4_h_prop_term | Proportional term for the PI controller for the heating coil in VAV4
vav4_h_int_term | Integral term for the PI controller for the heating coil in VAV4
ahu1_sa_sp_per | Setpoint for the percent outdoor air for AHU1
ahu1_sa_kp | Proportional gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_ki | Integral gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_kd | Derivative gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_ubias | Bias term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_sp_high | Upper limit on the percent outdoor air for AHU1
ahu1_sa_sp_low | Lower limit on the percent outdoor air for AHU1
ahu1_sa_pv_per | Actual percent outdoor air for AHU1
ahu1_sa_cv_v | Control signal for Damper6, the supply air damper, for AHU1
ahu1_sa_error_per | Difference between the actual and setpoint percent outdoor air for AHU1
ahu1_sa_cum_error_per | Integral error - sum of the difference between the actual and setpoint percent outdoor air for AHU1
ahu1_sa_prop_term | Proportional term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_int_term | Integral term for the PI controller for the percent outdoor air for AHU1
ahu2_sa_sp_per | Setpoint for the percent outdoor air for AHU2
ahu2_sa_kp | Proportional gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_ki | Integral gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_kd | Derivative gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_ubias | Bias term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_sp_high | Upper limit on the percent outdoor air for AHU2
ahu2_sa_sp_low | Lower limit on the percent outdoor air for AHU2
ahu2_sa_pv_per | Actual percent outdoor air for AHU2
ahu2_sa_cv_v | Control signal for Damper7, the supply air damper, for AHU2
ahu2_sa_error_per | Difference between the actual and setpoint percent outdoor air for AHU2
ahu2_sa_cum_error_per | Integral error - sum of the difference between the actual and setpoint percent outdoor air for AHU2
ahu2_sa_prop_term | Proportional term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_int_term | Integral term for the PI controller for the percent outdoor air for AHU2
ahu1_n_pr | Number of timesteps between setpoint changes for pressure reset for the supply fan in AHU1
ahu1_thresh_high_pr | Threshold on the VAV dampers that indicates more cooling is needed (the positions of either damper is above this threshold)
ahu1_thresh_low_pr | Threshold on the VAV dampers that indicates less cooling is needed (the positions of both dampers are below this threshold)
ahu1_delta_pr | Magnitude of the change of the pressure setpoint for the supply fan in AHU1
ahu2_n_pr | Number of timesteps between setpoint changes for pressure reset for the supply fan in AHU2
ahu2_thresh_high_pr | Threshold on the VAV dampers that indicates more cooling is needed (the positions of either damper is above this threshold)
ahu2_thresh_low_pr | Threshold on the VAV dampers that indicates less cooling is needed (the positions of both dampers are below this threshold)
ahu2_delta_pr | Magnitude of the change of the pressure setpoint for the supply fan in AHU2
vav1_fr_sp | Temperature setpont for the air leaving ZS1
vav1_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV1
vav1_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV1
vav1_fr_pv | Actual temperature leaving ZS1
vav1_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV1
vav1_fr_error | Difference between the actual and setpoint temperatures for ZS1
vav1_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
vav1_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav2_fr_sp | Temperature setpont for the air leaving ZS2
vav2_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV2
vav2_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV2
vav2_fr_pv | Actual temperature leaving ZS2
vav2_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV2
vav2_fr_error | Difference between the actual and setpoint temperatures for ZS2
vav2_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
vav2_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav3_fr_sp | Temperature setpont for the air leaving ZS3
vav3_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV3
vav3_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV3
vav3_fr_pv | Actual temperature leaving ZS3
vav3_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV3
vav3_fr_error | Difference between the actual and setpoint temperatures for ZS3
vav3_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
vav3_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav4_fr_sp | Temperature setpont for the air leaving ZS4
vav4_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV4
vav4_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV4
vav4_fr_pv | Actual temperature leaving ZS4
vav4_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV4
vav4_fr_error | Difference between the actual and setpoint temperatures for ZS4
vav4_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
vav4_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav1_tr_sp | Temperature setpont for the air leaving ZS1
vav1_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV1
vav1_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV1
vav1_tr_pv | Actual temperature leaving ZS1
vav1_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV1
vav1_tr_error | Difference between the actual and setpoint temperatures for ZS1
vav1_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
vav1_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav2_tr_sp | Temperature setpont for the air leaving ZS2
vav2_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV2
vav2_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV2
vav2_tr_pv | Actual temperature leaving ZS2
vav2_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV2
vav2_tr_error | Difference between the actual and setpoint temperatures for ZS2
vav2_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
vav2_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav3_tr_sp | Temperature setpont for the air leaving ZS3
vav3_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV3
vav3_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV3
vav3_tr_pv | Actual temperature leaving ZS3
vav3_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV3
vav3_tr_error | Difference between the actual and setpoint temperatures for ZS3
vav3_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
vav3_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav4_tr_sp | Temperature setpont for the air leaving ZS4
vav4_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV4
vav4_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV4
vav4_tr_pv | Actual temperature leaving ZS4
vav4_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV4
vav4_tr_error | Difference between the actual and setpoint temperatures for ZS4
vav4_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
vav4_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
zs1_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
zs1_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs2_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
zs2_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs4_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
zs4_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs3_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
zs3_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV3

## parameters
index | row of the data
time | Date and time of the data
ahu_dp | Differential pressure measurement in the secondary loop by the AHU coils
ahu1_cc_out_rtd | Temperature of the propylene glycol leaving the cooling coil in AHU1
ahu1_cc_rtd | Temperature of the air just after the cooling coil in AHU1
ahu1_f_cc | Flow rate of PG through the cooling coil in AHU1
ahu1_f_ra | Return airflow rate in AHU1
ahu1_f_sa | Supply airflow rate in AHU1
ahu1_fan_power | Power consumption of the AHU1 supply fan
ahu1_heat_c | Control signal for the electric heater in AHU1
ahu1_heat_power | Power consumption of the electric heater in AHU1
ahu1_heat_rtd | Temperature downstream of the electric heater in AHU1
ahu1_in_rtd | Temperature at the inlet of AHU1, after the return and supply air are mixed
ahu1_on | On/off control signal for the AHU1 supply fan
ahu1_out_rtd | Temperature downstream of AHU1
ahu1_p_down | Duct static pressure downstream of AHU1
ahu1_p_up | Static pressure upstream of the supply fan in AHU1
ahu1_rh_down | Relative humidity downstream of AHU1
ahu1_rh_ra | Relative humidity of the return air in AHU1
ahu1_rh_sa | Relative humidity of the supply air in AHU1
ahu1_rh_up | Relative humidity upstream of the supply fan in AHU1, after the return and supply air are mixed
ahu1_t_ra | Temperature of the return air in AHU1
ahu1_t_sa | Temperature of the supply air in AHU1
ahu1_tdb_ra | Dry bulb temperature of the return air in AHU1; same probe as ahu1_rh_ra
ahu1_tdb_sa | Dry bulb temperature of the supply air in AHU1; same probe as ahu1_rh_sa
ahu1_vfd | Speed of the AHU1 supply fan
ahu2_cc_in_rtd | Temperature of the propylene glycol entering the cooling coil in AHU1
ahu2_cc_out_rtd | Temperature of the propylene glycol leaving the cooling coil in AHU2
ahu2_cc_rtd | Temperature of the air just after the cooling coil in AHU2
ahu2_f_cc | Flow rate of PG through the cooling coil in AHU2
ahu2_f_ra | Return airflow rate in AHU2
ahu2_f_sa | Supply airflow rate in AHU2
ahu2_fan_power | Power consumption of the AHU2 supply fan
ahu2_heat_c | Control signal for the electric heater in AHU2
ahu2_heat_power | Power consumption of the electric heater in AHU2
ahu2_heat_rtd | Temperature downstream of the electric heater in AHU2
ahu2_in_rtd | Temperature at the inlet of AHU2, after the return and supply air are mixed
ahu2_on | On/off control signal for the AHU2 supply fan
ahu2_out_rtd | Temperature downstream of AHU2
ahu2_p_down | Duct static pressure downstream of AHU2
ahu2_p_up | Static pressure upstream of the supply fan in AHU2
ahu2_rh_down | Relative humidity downstream of AHU2
ahu2_rh_ra | Relative humidity of the return air in AHU2
ahu2_rh_up | Relative humidity upstream of the supply fan in AHU2, after the return and supply air are mixed
ahu2_t_ra | Temperature of the return air in AHU2
ahu2_t_sa | Temperature of the supply air in AHU2
ahu2_tdb_ra | Dry bulb temperature of the return air in AHU2; same probe as ahu2_rh_ra
ahu2_vfd | Speed of the AHU2 supply fan
ch1_c_out_rtd | Temperature of the water leaving the condenser in Chiller1
ch1_e_in_rtd | Temperature of the PG returning to both Chiller1 and Chiller2
ch1_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller1
ch1_f_c | Flow rate of the water through the condenser in Chiller1
ch1_f_e | Flow rate of the PG through the evaporator in Chiller1
ch1_on | On/off control signal for Chiller1
ch1_power | Power consumption of Chiller1
ch1_t_reset | Control to enable remote temperature setpoint for Chiller1
ch1_t_sp | Remote temperature setpoint for Chiller1
ch2_c_out_rtd | Temperature of the water leaving the condenser in Chiller2
ch2_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller2
ch2_f_c | Flow rate of the water through the condenser in Chiller2
ch2_f_e | Flow rate of the PG through the evaporator in Chiller2
ch2_on | On/off control signal for Chiller2
ch2_power | Power consumption of Chiller2
ch2_t_reset | Control to enable remote temperature setpoint for Chiller2
ch2_t_sp | Remote temperature setpoint for Chiller2
cl_f | Flow rate of water in the condensing loop
cw_in_rtd | Temperature of the chilled water entering the condensing loop
d10_pos_c | Control signal for the position of Damper10
d10_pos_fb | Feedback signal for the position of Damper10
d11_pos_c | Control signal for the position of Damper11
d11_pos_fb | Feedback signal for the position of Damper11
d15_pos_c | Control signal for the position of Damper15
d15_pos_fb | Feedback signal for the position of Damper15
d16_pos_c | Control signal for the position of Damper16
d16_pos_fb | Feedback signal for the position of Damper16
d17_pos_c | Control signal for the position of Damper17
d17_pos_fb | Feedback signal for the position of Damper17
d18_pos_c | Control signal for the position of Damper18
d18_pos_fb | Feedback signal for the position of Damper18
d2_pos_c | Control signal for the position of Damper2
d2_pos_fb | Feedback signal for the position of Damper2
d3_pos_c | Control signal for the position of Damper3
d3_pos_fb | Feedback signal for the position of Damper3
d4_pos_c | Control signal for the position of Damper4
d4_pos_fb | Feedback signal for the position of Damper4
d5_pos_c | Control signal for the position of Damper5
d5_pos_fb | Feedback signal for the position of Damper5
d6_pos_c | Control signal for the position of Damper6
d6_pos_fb | Feedback signal for the position of Damper6
d7_pos_c | Control signal for the position of Damper7
d7_pos_fb | Feedback signal for the position of Damper7
d8_pos_c | Control signal for the position of Damper8
d8_pos_fb | Feedback signal for the position of Damper8
dx_c1 | On/off signal for Compressor1 in the DX system
dx_c1_power | Partial measurement of power consumption of Compressor1 in the DX system
dx_c1_tsc1 | First temperature measurement used to estimate subcool in Compressor1 in the DX system
dx_c1_tsc2 | Second temperature measurement used to estimate subcool in Compressor1 in the DX system
dx_c1_tsh1 | First temperature measurement used to estimate superheat in Compressor1 in the DX system
dx_c1_tsh2 | Second temperature measurement used to estimate superheat in Compressor1 in the DX system
dx_c2 | On/off signal for Compressor2 in the DX system
dx_c2_power | Partial measurement of power consumption of Compressor2 in the DX system
dx_c2_tsc1 | First temperature measurement used to estimate subcool in Compressor2 in the DX system
dx_c2_tsc2 | Second temperature measurement used to estimate subcool in Compressor2 in the DX system
dx_c2_tsh1 | First temperature measurement used to estimate superheat in Compressor2 in the DX system
dx_c2_tsh2 | Second temperature measurement used to estimate superheat in Compressor2 in the DX system
dx_ds_c | Control signal for Compressor1 in the DX system
dx_m_cs | No longer used
dx_m_sclk | No longer used
dx_sp_cs | No longer used
dx_sp_din | No longer used
dx_sp_sclk | No longer used
dx_sp_spi | No longer used
dx_z_cs | No longer used
dx_z_din | No longer used
dx_z_sclk | No longer used
dx_z_spi | No longer used
exf1_f | Airflow rate at ExhaustFan1
exf1_on | On/off control for ExhaustFan1
exf1_p_down | Pressure downstream of ExhaustFan1
exf1_p_up | Pressure upstream of ExhaustFan1
exf1_power | Power consumption of ExhaustFan1
exf1_t_in | Temperature upstream of ExhaustFan1
exf1_vfd | Speed of ExhaustFan1
exf2_f | Airflow rate at ExhaustFan2
exf2_on | On/off control for ExhaustFan2
exf2_p_down | Pressure downstream of ExhaustFan2
exf2_p_up | Pressure upstream of ExhaustFan2
exf2_power | Power consumption of ExhaustFan2
exf2_t_in | Temperature upstream of ExhaustFan2
exf2_vfd | Speed of ExhaustFan2
hw_rtd | Temperature of the hot water entering the lab
hx1_f_hw | Flow rate of the hot water in HeatExchanger1
hx1_f_pg | Flow rate of the PG in HeatExchanger1
hx1_hw_rtd | Temperature of the hot water at the outlet of HeatExchanger1
hx1_pg_rtd | Tempeature of the PG at the outlet of HeatExchanger1
hx2_cw_rtd | Temperature of the chilled water at the outlet of HeatExchanger2
hx2_hw_rtd | Temperature of the hot water at the outlet of HeatExchanger2
hx3_cw_rtd | Temperature of the chilled water at the outlet of HeatExchanger3
hx3_f_cw | Flow rate of the chilled water through HeatExchanger3
hx3_f_pg | Flow rate of the PG through HeatExchanger3
hx3_pg_rtd | Temperature of the PG at the outlet of HeatExchanger3
indoor_p | Measurement of pressure in the IBAL
indoor_rh | Measurement of the relative humidity in the IBAL
indoor_rtd | Measurement of the temperature in the IBAL
mcc_run | On/off signal for the harmonic filter in the MCC
mcc_run_fb | Feedback for the on/off signal for the harmonic filter in the MCC
oau_cc_rtd | Air temperature downstream of the DX cooling coil in the OAU
oau_f_out | Airflow rate exhausting to the outdoors from the OAU
oau_fan_power | Power consumption of the OAU fan
oau_fz_in | Return signal from freezestat
oau_fz_out | Voltage signal to freezestat
oau_heat_c | Control signal for the electric heater in the OAU
oau_heat_power | Partial measurement of power consumption of the electric heater in the OAU
oau_hs_rtd | Temperature of the air just downstream of the electric heater in the OAU
oau_in_rtd | Temperatutre of the air at the inlet of the OAU, after the return and supply air mix
oau_on | On/off control signal for the OAU fan
oau_out_rtd | Temperature at the outlet of the OAU
oau_p_down | Static pressure downstream of the OAU fan
oau_p_up | Static pressure upstream of the OAU fan
oau_rh | Relative humidity at the outlet of the OAU
oau_t_out | Temperature of the air exhausting to the outdoors from the OAU
oau_vfd | Speed of the OAU fan
outdoor_rh | Relative humidity of the outdoor air
outdoor_rtd | Temperature of the outdoor air
pl_f | Flow rate in the primary loop
pl_ftemp | No longer used
pl_in_rtd | Temperautre of the PG entering (returning to) the primary loop
pl_out_rtd | Temperature of the PG leaving the primary loop
pump1_on | On/off control signal for Pump1
pump1_p_down | Pressure downstream of Pump1
pump1_p_up | Pressure upstream of Pump1
pump1_power | Power consumption of Pump1
pump1_vfd | Speed of Pump1
pump2_on | On/off control signal for Pump2
pump2_p_down | Pressure downstream of Pump2
pump2_p_up | Pressure upstream of Pump2
pump2_power | Power consumption of Pump2
pump2_vfd | Speed of Pump2
pump3_dp | Differential pressure across the secondary loop
pump3_on | On/off control signal for Pump3
pump3_out_rtd | Temperature downstream of Pump3
pump3_p_down | Pressure downstream of Pump3
pump3_p_up | Pressure upstream of Pump3
pump3_power | Power consumption of Pump3
pump3_vfd | Speed of Pump3
pump4_on | On/off control signal for Pump4
pump4_out_rtd | Temperature downstream of Pump4
pump4_p_down | Pressure downstream of Pump4
pump4_p_up | Pressure upstream of Pump4
pump4_power | Power consumption of Pump4
pump4_vfd | Speed of Pump4
pump5_on | On/off control signal for Pump5
pump5_p_down | Pressure downstream of Pump5
pump5_p_up | Pressure upstream of Pump5
pump5_power | Power consumption of Pump5
pump5_vfd | Speed of Pump5
sl_f | Flow rate in the secondary loop
sl_ftemp | No longer used
sl_out_rtd | Temperature at the outlet of the secondary loop
timer | No longer used
tmc1_in_rtd | Temperature of the water entering the Thermal Mass Coil 1
tmc1_out_rtd | Temperature of the water leaving Thermal Mass Coil 1
tmc1_pos_c | Position of the throttling valve in Thermal Mass Coil 1
tmc1_pump_on | On/off control signal for the pump in Thermal Mass Coil 1
tmc2_in_rtd | Temperature of the water entering the Thermal Mass Coil 2
tmc2_out_rtd | Temperature of the water leaving Thermal Mass Coil 2
tmc2_pos_c | Position of the throttling valve in Thermal Mass Coil 2
tmc2_pump_on | On/off control signal for the pump in Thermal Mass Coil 2
tmc3_in_rtd | Temperature of the water entering the Thermal Mass Coil 3
tmc3_out_rtd | Temperature of the water leaving Thermal Mass Coil 3
tmc3_pos_c | Position of the throttling valve in Thermal Mass Coil 3
tmc3_pump_on | On/off control signal for the pump in Thermal Mass Coil 3
tmc4_in_rtd | Temperature of the water entering the Thermal Mass Coil 4
tmc4_out_rtd | Temperature of the water leaving Thermal Mass Coil 4
tmc4_pos_c | Position of the throttling valve in Thermal Mass Coil 4
tmc4_pump_on | On/off control signal for the pump in Thermal Mass Coil 4
ts_f | Flow rate through the thermal storage tank
ts_in_rtd | Temperature of the PG entering the thermal storage tank
ts_meter | Ice meter reading of the inventory in the thermal storage tank
ts_out_rtd | Temperature of the PG leaving the thermal storage tank
v1_pos_c | Control signal for the position of Valve1
v1_pos_fb | Feedback signal for the position of Valve1
v10_pos_c | Control signal for the position of Valve10
v10_pos_fb | Feedback signal for the position of Valve10
v11_pos_c | Control signal for the position of Valve11
v11_pos_fb | Feedback signal for the position of Valve11
v12_pos_c | Control signal for the position of Valve12
v12_pos_fb | Feedback signal for the position of Valve12
v13_pos_c | Control signal for the position of Valve13
v13_pos_fb | Feedback signal for the position of Valve13
v14_pos_c | Control signal for the position of Valve14
v14_pos_fb | Feedback signal for the position of Valve14
v15_pos_c | Control signal for the position of Valve15
v15_pos_fb | Feedback signal for the position of Valve15
v16_pos_c | Control signal for the position of Valve16
v16_pos_fb | Feedback signal for the position of Valve16
v17_pos_c | Control signal for the position of Valve17
v17_pos_fb | Feedback signal for the position of Valve17
v18_pos_c | Control signal for the position of Valve18
v18_pos_fb | Feedback signal for the position of Valve18
v19_pos_c | Control signal for the position of Valve19
v19_pos_fb | Feedback signal for the position of Valve19
v2_pos_c | Control signal for the position of Valve2
v2_pos_fb | Feedback signal for the position of Valve2
v20_pos_c | Control signal for the position of Valve20
v20_pos_fb | Feedback signal for the position of Valve20
v3_pos_c | Control signal for the position of Valve3
v3_pos_fb | Feedback signal for the position of Valve3
v4_pos_c | Control signal for the position of Valve4
v4_pos_fb | Feedback signal for the position of Valve4
v5_pos_c | Control signal for the position of Valve5
v5_pos_fb | Feedback signal for the position of Valve5
v6_pos_c | Control signal for the position of Valve6
v6_pos_fb | Feedback signal for the position of Valve6
v7_pos_c | Control signal for the position of Valve7
v7_pos_fb | Feedback signal for the position of Valve7
v8_pos_c | Control signal for the position of Valve8
v8_pos_fb | Feedback signal for the position of Valve8
v9_pos_c | Control signal for the position of Valve9
v9_pos_fb | Feedback signal for the position of Valve9
vav1_f | Airflow rate through VAV1
vav1_heat_c | Control signal for the electric reheat in VAV1
vav1_heat_power | Power consumption of the electric reheat in VAV1
vav1_out_rtd | Temperature of the air downstream of VAV1
vav1_t_in | Temperature of the air upstream of VAV1
vav2_f | Airflow rate through VAV2
vav2_heat_c | Control signal for the electric reheat in VAV2
vav2_heat_power | Power consumption of the electric reheat in VAV2
vav2_out_rtd | Temperature of the air downstream of VAV2
vav2_t_in | Temperature of the air upstream of VAV2
vav3_f | Airflow rate through VAV3
vav3_heat_c | Control signal for the electric reheat in VAV3
vav3_heat_power | Power consumption of the electric reheat in VAV3
vav3_out_rtd | Temperature of the air downstream of VAV3
vav3_t_in | Temperature of the air upstream of VAV3
vav4_f | Airflow rate through VAV4
vav4_heat_c | Control signal for the electric reheat in VAV4
vav4_heat_power | Power consumption of the electric reheat in VAV4
vav4_out_rtd | Temperature of the air downstream of VAV4
vav4_t_in | Temperature of the air upstream of VAV4
vch1_pos_fb | No longer used
vch2_pos_fb | No longer used
vsh_in | Return signal for the shutoff valves for the chilled and hot water
vsh_out | Control signal for the shutoff valves for the chilled and hot water
zs1_heat_c | Control signal for the electric heater in ZS1
zs1_heat_power | Power consumption of the electric heater in ZS1
zs1_heat_rtd | Temperature of the air downstream of the electric heater in ZS1
zs1_out_rtd | Temperature of the air downstream of ZS1 (zone temperature)
zs1_rh | Relative humidity of the air downstream of ZS1 (zone relative humidity)
zs2_heat_c | Control signal for the electric heater in ZS2
zs2_heat_power | Power consumption of the electric heater in ZS2
zs2_heat_rtd | Temperature of the air downstream of the electric heater in ZS2
zs2_out_rtd | Temperature of the air downstream of ZS2 (zone temperature)
zs2_rh | Relative humidity of the air downstream of ZS2 (zone relative humidity)
zs3_heat_c | Control signal for the electric heater in ZS3
zs3_heat_power | Power consumption of the electric heater in ZS3
zs3_heat_rtd | Temperature of the air downstream of the electric heater in ZS3
zs3_out_rtd | Temperature of the air downstream of ZS3 (zone temperature)
zs3_rh | Relative humidity of the air downstream of ZS3 (zone relative humidity)
zs4_heat_c | Control signal for the electric heater in ZS4
zs4_heat_power | Power consumption of the electric heater in ZS4
zs4_heat_rtd | Temperature of the air downstream of the electric heater in ZS4
zs4_out_rtd | Temperature of the air downstream of ZS4 (zone temperature)
zs4_rh | Relative humidity of the air downstream of ZS4 (zone relative humidity)
cl_t_sp_f | Temperature setpoint of the water in the condensing loop
cl_t_kp | Proportional gain for the PI controller for the temperature of the condensing loop
cl_t_ki | Integral gain for the PI controller for the temperature of the condensing loop
cl_t_kd | Derivative gain for the PI controller for the temperature of the condensing loop
cl_t_ubias | Bias term for the PI controller for the temperature of the condensing loop
cl_t_sp_high | Upper limit on the temperature setpoint in the condensing loop
cl_t_sp_low | Lower limit on the temperature setpoint in the condensing loop
cl_t_pv_f | Actual temperature being controlled in the condensing loop
cl_t_cv_v | Control signal for Valve3, the control valve, in the condensing loop
cl_t_error_f | Difference between the actual and setpoint temperatures in the condensing loop
cl_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures in the condensing loop
cl_t_prop_term | Proportional term in the PI controller for the condensing loop
cl_t_int_term | Integral term in the PI controller for the condensing loop
cl_pi_mode | PI mode of the CL controller for V3; 1 = Auto, 0 = Manual
cl_overall_mode | Overall mode of the CL controller (automatically turn pump on, open valves, etc.); 1 = Auto, 0 = Manual
sl_t_sp_f | Temperature setpoint of the PG in the secondary loop
sl_t_kp | Proportional gain for the PI controller for the temperature of the secondary loop
sl_t_ki | Integral gain for the PI controller for the temperature of the secondary loop
sl_t_kd | Derivative gain for the PI controller for the temperature of the secondary loop
sl_t_ubias | Bias term for the PI controller for the temperature of the secondary loop
sl_t_sp_high | Upper limit on the temperature setpoint in the secondary loop
sl_t_sp_low | Lower limit on the temperature setpoint in the secondary loop
sl_t_pv_f | Actual temperature being controlled in the secondary loop
sl_t_cv_v | Control signal for Valve9, the control valve, in the secondary loop
sl_t_error_f | Difference between the actual and setpoint temperatures in the secondary loop
sl_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures in the secondary loop
sl_DB | No longer used
sl_vfd_sp_v | Pump speed setpoint for the secondary loop pump
sl_vfd_kp | Proportional gain for the PI controller for the pump speed in the secondary loop
sl_vfd_ki | Integral gain for the PI controller for the pump speed in the secondary loop
sl_vfd_kd | Derivative gain for the PI controller for the pump speed in the secondary loop
sl_vfd_ubias | Bias for the PI controller for the pump speed in the secondary loop
sl_vfd_sp_high | Upper limit on the pump speed in the secondary loop
sl_vfd_sp_low | Lower limit on the pump speed in the secondary loop
sl_vfd_pv_v | Actual pump speed being controlled in the secondary loop
sl_vfd_cv_hz | Control signal for Pump3, the secondary loop pump
sl_vfd_error_v | Difference between the actual and setpoint pump speeds in the secondary loop
sl_vfd_cum_error_v | Integral error term - sum of the difference between the actual and setpoint pump speeds in the secondary loop
sl_n_pr | Number of timesteps between setpoint changes for pressure reset in the secondary loop
sl_thresh_low_pr | Threshold on the cooling coil valves that indicates less cooling is needed (the positions of both valves are below this threshold)
sl_thresh_high_pr | Threshold on the cooling coil valves that indicates more cooling is needed (the position of at least one valve exceeds this threshold)
sl_delta_pr | Magnitude of the change of the pressure setpoint in the secondary loop
sl_overall_mode | Overall mode of the SL controller (automatically turn pump on, open valves, etc. based on building load); 1 = Auto, 0 = Manual
sl_pi_vfd_mode | PI mode of the SL controller for pump speed; 1 = Auto, 0 = Manual
sl_pi_v9_mode | PI mode of the SL controller for temperature via V9; 1 = Auto, 0 = Manual
sl_dp_mode | Mode for differential pressure reset for SL pump; 1 = Auto, 0 = Manual
ts_end_charging | Flag to indicate that charging of the thermal storage tank is complete
ts_t_sp_f | Temperature setpoint of the PG leaving the thermal storage tank
ts_t_kp | Proportional gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_ki | Integral gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_kd | Derivative gain for the PI controller for the temperature leaving the thermal storage tank
ts_t_ubias | Bias term for the PI controller for the temperature leaving the thermal storage tank
ts_t_sp_high | Upper limit on the temperature setpoint of the PG leaving the thermal storage tank
ts_t_sp_low | Lower limit on the temperature setpoint of the PG leaving the thermal storage tank
ts_t_pv_f | Actual temperature being controlled after the thermal storage tank
ts_t_cv_v | Control signal for Valve8, the control valve, for the PG leaving the thermal storage tank
ts_t_error_f | Difference between the actual and setpoint temperatures leaving the thermal storage tank
ts_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures leaving the thermal storage tank
ts_mode | Overall mode for the TS controller; 1 = Auto, 0 = Manual
hx1_t_sp_f | Temperature setpoint of the PG leaving HX1
hx1_t_kp | Proportional gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_ki | Integral gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_kd | Derivative gain for the PI controller for the temperature of the PG leaving HX1
hx1_t_ubias | Bias term for the PI controller for the temperature of the PG leaving HX1
hx1_t_sp_high | Upper limit on the temperature setpoint of the PG leaving HX1
hx1_t_sp_low | Lower limit on the temperature setpoint of the PG leaving HX1
hx1_t_pv_f | Actual temperature of the PG being controlled in HX1
hx1_t_dt_f | No longer used
hx1_t_error_f | Difference between the actual and setpoint temperatures of the PG leaving HX1
hx1_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures of the PG leaving HX1
hx1_t_cv_v | Control signal for Valve10, the control valve, in the PG side of HX1
hx1_load_sp_kw | Load setpoint for HX1
hx1_load_pv_inst_kw | Actual load generated by HX1
hx1_load_kp | Proportional gain for the PI controller for the load generated by HX1
hx1_load_ki | Integral gain for the PI controller for the load generated by HX1
hx1_load_kd | Derivative gain for the PI controller for the load generated by HX1
hx1_load_ubias | Bias term for the PI controller for the load generated by HX1
hx1_load_sp_high | Upper limit on the load setpoint in HX1
hx1_load_sp_low | Lower limit on the load setpoint in HX1
hx1_load_pv_avg_kw | Averaged actual load generated by HX1
hx1_load_cv_v | Control signal for Valve11, the control valve, in HX1
hx1_load_dq_kw | No longer used
hx1_load_error_kw | Difference between the actual and setpoint loads in HX1
hx1_load_cum_error_kw | Integral error term - sum of the difference between the actual and setpoint loads in HX1
ch1_t_sp_f | Temperature setpoint for Chiller1
ch1_overall_mode | Overall mode of the Chiller1 controller (automatically turn pump on, open valves, etc. based on building load); 1 = Auto, 0 = Manual
ch1_chwst_mode | Mode for chiller setpoint temperature reset; 1 = Auto, 0 = Manual
ch2_t_sp_f | Temperature setpoint for Chiller2
ch2_overall_mode | Overall mode of the Chiller2 controller (automatically turn pump on, open valves, etc. based on building load); 1 = Auto, 0 = Manual
ch2_chwst_mode | Mode for chiller setpoint temperature reset; 1 = Auto, 0 = Manual
oau_h_t_sp_f | Temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_kp | Proportional gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_ki | Integral gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_kd | Derivative gain for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_ubias | Bias term for the PI controller for the temperature leaving the heating coil in the OAU
oau_h_t_sp_high | Upper limit on the temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_sp_low | Lower limit on the temperature setpoint of the air leaving the heating coil in the OAU
oau_h_t_pv_f | Actual temperature of the air leaving the heating coil in the OAU
oau_h_t_cv_v | Control signal for the OAU heater
oau_h_t_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in the OAU
oau_h_t_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in the OAU
oau_h_prop_term | Proportional term in the PI controller for the heating coil in the OAU
oau_h_int_term | Integral term in the PI controller for the heating coil in the OAU
oau_h_threshold | No longer used
oau_h_delay | No longer used
oau_h_dtheat | No longer used
oau_h_outdoor_rtd_mean | No longer used
oau_h_deriv_term | Derivative term in the PI controller for the heating coil in the OAU
oau_h_t_error_rate | Derivative error term - rate of change of the error
oau_h_pi_mode | PI mode of the OAU controller for the electric heater; 1 = Auto, 0 = Manual
oau_c_t_kd | Derivative gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_kp | Proportional gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_ki | Integral gain for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_ubias | Bias term for the cooling coil PI controller for the humidity ratio leaving the OAU
oau_c_t_sp_high | Upper limit on the humidity ratio leaving the OAU
oau_c_t_sp_low | Lower limit on the humidity ratio leaving the OAU
oau_c_t_sp_f | Setpoint humidity ratio of the air leaving the OAU
oau_c_t_pv_f | Actual humidity ratio of the air leaving the OAU
oau_c_t_cum_error_f | Integral error term - difference between the actual and setpoint humidity ratios of the air leaving the OAU
oau_c_prop_term | Proportional term in the PI controller for the heating coil in the OAU
oau_c_int_term | Integral term in the PI controller for the heating coil in the OAU
oau_c_delay | No longer used
oau_c_t_cv_v | Control signal for Compressor1 in the cooling coil in the OAU
oau_c_t_error_f | Difference between the actual and setpoint humidity ratios of the air leaving the OAU
oau_c_dt | no longer used
oau_c_delay2 | no longer used
oau_c_pi_mode | PI mode of the OAU controller for the cooling coil; 1 = Auto, 0 = Manual
oau_w_rh_sp_per | Setpoint relative humidity of the air leaving the OAU
oau_w_rh_kp | Proportional gain for the humidifier PI controller in the OAU
oau_w_rh_ki | Integral gain for the humidifier PI controller in the OAU
oau_w_rh_kd | Derivative gain for the humidifier PI controller in the OAU
oau_w_rh_ubias | Bias term for the humidifier PI controller in the OAU
oau_w_rh_sp_high | Upper limit on the relative humidity leaving the OAU
oau_w_rh_sp_low | Lower limit on the relative humidity leaving the OAU
oau_w_rh_pv_per | Actual relative humidity leaving the OAU
oau_w_rh_cv_v | Control signal for Valve2, the control valve for the humidifier
oau_w_rh_error_per | Difference between the actual and setpoint relative humidity of the air leaving the OAU
oau_w_rh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint relative humidity of the air leaving the OAU
oau_w_prop_term | Proportional term in the PI controller for the humidifier in the OAU
oau_w_int_term | Integral term in the PI controller for the humidifier in the OAU
oau_w_pi_mode | PI mode of the OAU controller for the humidifier; 1 = Auto, 0 = Manual
oau_t_out_sp_f | Setpoint temperature of the air leaving the OAU
oau_rh_out_sp_per | Setpoint relative humidity of the air leaving the OAU
oau_read_from_file | Flag to indicate that the OAU setpoints should be read from file
oau_t_out_pv_f | Measured value of the controlled temperature for the OAU
oau_rh_out_pv_per | Measured value of the controlled relative humidity for the OAU
bc_n_sl_on | Number of timesteps that the secondary loop pump has to be on for there to be a building load
bc_n_q_mean | Number of timesteps to include in the calculation of the average load
bc_n_chiller_fault | Number of chiller fault flags before a chiller is considered to be in a fault status
bc_n_pump3_max | No longer used
bc_n_stage_up | Number of timesteps in the current stage before a chiller can be staged up
bc_n_stage_down | Number of timesteps in the current stage before a chiller can be staged down
bc_q1_min | Minimum load that allows Chiller1 to be enabled
bc_q1_sd | Load at which Chiller1 is staged down (turned off)
bc_q1_su | No longer used
bc_q2_min | Minimum load that allows Chiller2 to be enabled
bc_q2_sd | Load at which Chiller2 is staged down (turned off)
bc_q2_su | No longer used
bc_q3_min | No longer used
bc_q3_sd | No longer used
bc_q3_su | No longer used
bc_v10_sp | No longer used
bc_dt_sl | Value by which to offset the chiller setpoint temperature for the secondary loop
bc_max_plant_load_kw | No longer used
bc_pump3_max_vfd | No longer used
bc_n_trans | Number of timesteps for transition between stages
bc_n_viol | Number of timesteps that a violation has to occur before the stage can change
stage_up_down_count | Number of timesteps when a stage up or down is requested
stage_stage | The current stage that the chillers are in
stage_allow_stage_up_time | Flag to indicate that a chiller can stage up
stage_allow_stage_down_time | Flag to indicate that a chiller can stage down
stage_allow_stage_up_pump3 | No longer used
stage_allow_stage_down_temp | No longer used
zs1_qs_sp_w | Sensible load setpoint for ZS1
zs1_qs_pv_w | Actual sensible load in ZS1
zs1_qs_ca_a | Control signal for the heating coil in ZS1
zs1_qs_error_w | Difference between the actual and setpoint sensible loads in ZS1
zs1_qs_cum_error_w | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS1
zs1_ql_sp_w | Latent load setpoint for ZS1
zs1_ql_pv_w | Actual latent load in ZS1
zs1_ql_cv_v | Control signal for Valve14, the control valve for the humidifier in ZS1
zs1_ql_error_w | Difference between the actual and setpoint latent loads in ZS1
zs1_ql_cum_error_w | Integral error - sum of the difference between the actual and setpoint latent loads in ZS1
zs1_qs_kp | Proportional gain for the PI controller for the sensible load in ZS1
zs1_qs_ki | Integral gain for the PI controller for the sensible load in ZS1
zs1_qs_kd | Derivative gain for the PI controller for the sensible load in ZS1
zs1_qs_ubias | Bias term for the PI controller for the sensible load in ZS1
zs1_qs_sp_hi | Upper limit on the sensible load setpoint in ZS1
zs1_qs_sp_low | Lower limit on the sensible load setpoint in ZS1
zs1_ql_kp | Proportional gain for the PI controller for the latent load in ZS1
zs1_ql_ki | Integral gain for the PI controller for the latent load in ZS1
zs1_ql_kd | Derivative gain for the PI controller for the latent load in ZS1
zs1_ql_ubias | Bias term for the PI controller for the latent load in ZS1
zs1_ql_sp_hi | Upper limit on the latent load setpoint in ZS1
zs1_ql_sp_low | Lower limit on the latent load setpoint in ZS1
zs1_t_sp_f | Setpoint temperature for the air leaving ZS1
zs1_rh_sp_per | Relative humidity setpoint for the air leaving ZS1
zs1_qst_sp_f | Temperature setpoint for sensible load control of ZS1
zs1_qst_pv_f | Actual temperature in ZS1
zs1_qst_ca_a | Control signal for the heating coil in ZS1
zs1_qst_error_f | Difference between the actual and setpoint temperatures for sensible load control in ZS1
zs1_qst_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures for sensible load control in ZS1
zs1_qst_kp | Proportional gain for the PI controller for temperature control of the sensible load in ZS1
zs1_qst_ki | Integral gain for the PI controller for temperature control of the sensible load in ZS1
zs1_qst_kd | Derivative gain for the PI controller for temperature control of the sensible load in ZS1
zs1_qst_ubias | Bias term for the PI controller for temperature control of the sensible load in ZS1
zs1_qst_sp_hi | Upper limit for the setpoint for temperature control of the sensible load in ZS1
zs1_qst_sp_low | Lower limit for the setpoint for temperature control of the sensible load in ZS1
zs1_qlrh_sp_per | RH setpoint for latent load control of ZS1
zs1_qlrh_pv_per | Actual RH in ZS1
zs1_qlrh_cv_v | Control signal for Valve14, the control valve for the humidifier in ZS1
zs1_qlrh_error_per | Difference between the actual and setpoint RH for latent load control in ZS1
zs1_qlrh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint RH for latent load control in ZS1
zs1_qlrh_kp | Proportional gain for the PI controller for RH control of the latent load in ZS1
zs1_qlrh_ki | Integral gain for the PI controller for RH control of the latent load in ZS1
zs1_qlrh_kd | Derivative gain for the PI controller for RH control of the latent load in ZS1
zs1_qlrh_ubias | Bias term for the PI controller for RH control of the latent load in ZS1
zs1_qlrh_sp_hi | Upper limit for the setpoint for RH control of the latent load in ZS1
zs1_qlrh_sp_low | Lower limit for the setpoint for RH control of the latent load in ZS1
zs1_pi_qst_mode | PI mode for temperature control of the sensible load in ZS1; 1 = Auto, 0 = Manual
zs1_pi_qlrh_mode | PI mode for RH control of the latent load in ZS1; 1 = Auto, 0 = Manual
zs2_qs_sp_w | Sensible load setpoint for ZS2
zs2_qs_pv_w | Actual sensible load in ZS2
zs2_qs_ca_a | Control signal for the heating coil in ZS2
zs2_qs_error_w | Difference between the actual and setpoint sensible loads in ZS2
zs2_qs_cum_error_w | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS2
zs2_ql_sp_w | Latent load setpoint for ZS2
zs2_ql_pv_w | Actual latent load in ZS2
zs2_ql_cv_v | Control signal for Valve15, the control valve for the humidifier in ZS2
zs2_ql_error_w | Difference between the actual and setpoint latent loads in ZS2
zs2_ql_cum_error_w | Integral error - sum of the difference between the actual and setpoint latent loads in ZS2
zs2_qs_kp | Proportional gain for the PI controller for the sensible load in ZS2
zs2_qs_ki | Integral gain for the PI controller for the sensible load in ZS2
zs2_qs_kd | Derivative gain for the PI controller for the sensible load in ZS2
zs2_qs_ubias | Bias term for the PI controller for the sensible load in ZS2
zs2_qs_sp_hi | Upper limit on the sensible load setpoint in ZS2
zs2_qs_sp_low | Lower limit on the sensible load setpoint in ZS2
zs2_ql_kp | Proportional gain for the PI controller for the latent load in ZS2
zs2_ql_ki | Integral gain for the PI controller for the latent load in ZS2
zs2_ql_kd | Derivative gain for the PI controller for the latent load in ZS2
zs2_ql_ubias | Bias term for the PI controller for the latent load in ZS2
zs2_ql_sp_hi | Upper limit on the latent load setpoint in ZS2
zs2_ql_sp_low | Lower limit on the latent load setpoint in ZS2
zs2_rh_sp_per | Setpoint temperature for the air leaving ZS2
zs2_t_sp_f | Relative humidity setpoint for the air leaving ZS2
zs2_qst_sp_f | Temperature setpoint for sensible load control of ZS2
zs2_qst_pv_f | Actual temperature in ZS2
zs2_qst_ca_a | Control signal for the heating coil in ZS2
zs2_qst_error_f | Difference between the actual and setpoint temperatures for sensible load control in ZS2
zs2_qst_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures for sensible load control in ZS2
zs2_qst_kp | Proportional gain for the PI controller for temperature control of the sensible load in ZS2
zs2_qst_ki | Integral gain for the PI controller for temperature control of the sensible load in ZS2
zs2_qst_kd | Derivative gain for the PI controller for temperature control of the sensible load in ZS2
zs2_qst_ubias | Bias term for the PI controller for temperature control of the sensible load in ZS2
zs2_qst_sp_hi | Upper limit for the setpoint for temperature control of the sensible load in ZS2
zs2_qst_sp_low | Lower limit for the setpoint for temperature control of the sensible load in ZS2
zs2_qlrh_sp_per | RH setpoint for latent load control of ZS2
zs2_qlrh_pv_per | Actual RH in ZS2
zs2_qlrh_cv_v | Control signal for Valve15, the control valve for the humidifier in ZS2
zs2_qlrh_error_per | Difference between the actual and setpoint RH for latent load control in ZS2
zs2_qlrh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint RH for latent load control in ZS2
zs2_qlrh_kp | Proportional gain for the PI controller for RH control of the latent load in ZS2
zs2_qlrh_ki | Integral gain for the PI controller for RH control of the latent load in ZS2
zs2_qlrh_kd | Derivative gain for the PI controller for RH control of the latent load in ZS2
zs2_qlrh_ubias | Bias term for the PI controller for RH control of the latent load in ZS2
zs2_qlrh_sp_hi | Upper limit for the setpoint for RH control of the latent load in ZS2
zs2_qlrh_sp_low | Lower limit for the setpoint for RH control of the latent load in ZS2
zs2_pi_qst_mode | PI mode for temperature control of the sensible load in ZS2; 1 = Auto, 0 = Manual
zs2_pi_qlrh_mode | PI mode for RH control of the latent load in ZS2; 1 = Auto, 0 = Manual
zs3_qs_sp_w | Sensible load setpoint for ZS3
zs3_qs_pv_w | Actual sensible load in ZS3
zs3_qs_ca_a | Control signal for the heating coil in ZS3
zs3_qs_error_w | Difference between the actual and setpoint sensible loads in ZS3
zs3_qs_cum_error_w | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS3
zs3_ql_sp_w | Latent load setpoint for ZS3
zs3_ql_pv_w | Actual latent load in ZS3
zs3_ql_cv_v | Control signal for Valve16, the control valve for the humidifier in ZS3
zs3_ql_error_w | Difference between the actual and setpoint latent loads in ZS3
zs3_ql_cum_error_w | Integral error - sum of the difference between the actual and setpoint latent loads in ZS3
zs3_qs_kp | Proportional gain for the PI controller for the sensible load in ZS3
zs3_qs_ki | Integral gain for the PI controller for the sensible load in ZS3
zs3_qs_kd | Derivative gain for the PI controller for the sensible load in ZS3
zs3_qs_ubias | Bias term for the PI controller for the sensible load in ZS3
zs3_qs_sp_hi | Upper limit on the sensible load setpoint in ZS3
zs3_qs_sp_low | Lower limit on the sensible load setpoint in ZS3
zs3_ql_kp | Proportional gain for the PI controller for the latent load in ZS3
zs3_ql_ki | Integral gain for the PI controller for the latent load in ZS3
zs3_ql_kd | Derivative gain for the PI controller for the latent load in ZS3
zs3_ql_ubias | Bias term for the PI controller for the latent load in ZS3
zs3_ql_sp_hi | Upper limit on the latent load setpoint in ZS3
zs3_ql_sp_low | Lower limit on the latent load setpoint in ZS3
zs3_rh_sp_per | Setpoint temperature for the air leaving ZS3
zs3_t_sp_f | Relative humidity setpoint for the air leaving ZS3
zs3_qst_sp_f | Temperature setpoint for sensible load control of ZS3
zs3_qst_pv_f | Actual temperature in ZS3
zs3_qst_ca_a | Control signal for the heating coil in ZS3
zs3_qst_error_f | Difference between the actual and setpoint temperatures for sensible load control in ZS3
zs3_qst_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures for sensible load control in ZS3
zs3_qst_kp | Proportional gain for the PI controller for temperature control of the sensible load in ZS3
zs3_qst_ki | Integral gain for the PI controller for temperature control of the sensible load in ZS3
zs3_qst_kd | Derivative gain for the PI controller for temperature control of the sensible load in ZS3
zs3_qst_ubias | Bias term for the PI controller for temperature control of the sensible load in ZS3
zs3_qst_sp_hi | Upper limit for the setpoint for temperature control of the sensible load in ZS3
zs3_qst_sp_low | Lower limit for the setpoint for temperature control of the sensible load in ZS3
zs3_qlrh_sp_per | RH setpoint for latent load control of ZS3
zs3_qlrh_pv_per | Actual RH in ZS3
zs3_qlrh_cv_v | Control signal for Valve16, the control valve for the humidifier in ZS3
zs3_qlrh_error_per | Difference between the actual and setpoint RH for latent load control in ZS3
zs3_qlrh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint RH for latent load control in ZS3
zs3_qlrh_kp | Proportional gain for the PI controller for RH control of the latent load in ZS3
zs3_qlrh_ki | Integral gain for the PI controller for RH control of the latent load in ZS3
zs3_qlrh_kd | Derivative gain for the PI controller for RH control of the latent load in ZS3
zs3_qlrh_ubias | Bias term for the PI controller for RH control of the latent load in ZS3
zs3_qlrh_sp_hi | Upper limit for the setpoint for RH control of the latent load in ZS3
zs3_qlrh_sp_low | Lower limit for the setpoint for RH control of the latent load in ZS3
zs3_pi_qst_mode | PI mode for temperature control of the sensible load in ZS3; 1 = Auto, 0 = Manual
zs3_pi_qlrh_mode | PI mode for RH control of the latent load in ZS3; 1 = Auto, 0 = Manual
zs4_qs_sp_w | Sensible load setpoint for ZS4
zs4_qs_pv_w | Actual sensible load in ZS4
zs4_qs_ca_a | Control signal for the heating coil in ZS4
zs4_qs_error_w | Difference between the actual and setpoint sensible loads in ZS4
zs4_qs_cum_error_w | Integral error term - sum of the difference between the actual and setpoint sensible loads in ZS4
zs4_ql_sp_w | Latent load setpoint for ZS4
zs4_ql_pv_w | Actual latent load in ZS4
zs4_ql_cv_v | Control signal for Valve17, the control valve for the humidifier in ZS4
zs4_ql_error_w | Difference between the actual and setpoint latent loads in ZS4
zs4_ql_cum_error_w | Integral error - sum of the difference between the actual and setpoint latent loads in ZS4
zs4_qs_kp | Proportional gain for the PI controller for the sensible load in ZS4
zs4_qs_ki | Integral gain for the PI controller for the sensible load in ZS4
zs4_qs_kd | Derivative gain for the PI controller for the sensible load in ZS4
zs4_qs_ubias | Bias term for the PI controller for the sensible load in ZS4
zs4_qs_sp_hi | Upper limit on the sensible load setpoint in ZS4
zs4_qs_sp_low | Lower limit on the sensible load setpoint in ZS4
zs4_ql_kp | Proportional gain for the PI controller for the latent load in ZS4
zs4_ql_ki | Integral gain for the PI controller for the latent load in ZS4
zs4_ql_kd | Derivative gain for the PI controller for the latent load in ZS4
zs4_ql_ubias | Bias term for the PI controller for the latent load in ZS4
zs4_ql_sp_hi | Upper limit on the latent load setpoint in ZS4
zs4_ql_sp_low | Lower limit on the latent load setpoint in ZS4
zs4_rh_sp_per | Setpoint temperature for the air leaving ZS4
zs4_t_sp_f | Relative humidity setpoint for the air leaving ZS4
zs4_qst_sp_f | Temperature setpoint for sensible load control of ZS4
zs4_qst_pv_f | Actual temperature in ZS4
zs4_qst_ca_a | Control signal for the heating coil in ZS4
zs4_qst_error_f | Difference between the actual and setpoint temperatures for sensible load control in ZS4
zs4_qst_cum_error_f | Integral error term - sum of the difference between the actual and setpoint temperatures for sensible load control in ZS4
zs4_qst_kp | Proportional gain for the PI controller for temperature control of the sensible load in ZS4
zs4_qst_ki | Integral gain for the PI controller for temperature control of the sensible load in ZS4
zs4_qst_kd | Derivative gain for the PI controller for temperature control of the sensible load in ZS4
zs4_qst_ubias | Bias term for the PI controller for temperature control of the sensible load in ZS4
zs4_qst_sp_hi | Upper limit for the setpoint for temperature control of the sensible load in ZS4
zs4_qst_sp_low | Lower limit for the setpoint for temperature control of the sensible load in ZS4
zs4_qlrh_sp_per | RH setpoint for latent load control of ZS4
zs4_qlrh_pv_per | Actual RH in ZS4
zs4_qlrh_cv_v | Control signal for Valve17, the control valve for the humidifier in ZS4
zs4_qlrh_error_per | Difference between the actual and setpoint RH for latent load control in ZS4
zs4_qlrh_cum_error_per | Integral error term - sum of the difference between the actual and setpoint RH for latent load control in ZS4
zs4_qlrh_kp | Proportional gain for the PI controller for RH control of the latent load in ZS4
zs4_qlrh_ki | Integral gain for the PI controller for RH control of the latent load in ZS4
zs4_qlrh_kd | Derivative gain for the PI controller for RH control of the latent load in ZS4
zs4_qlrh_ubias | Bias term for the PI controller for RH control of the latent load in ZS4
zs4_qlrh_sp_hi | Upper limit for the setpoint for RH control of the latent load in ZS4
zs4_qlrh_sp_low | Lower limit for the setpoint for RH control of the latent load in ZS4
zs4_pi_qst_mode | PI mode for temperature control of the sensible load in ZS4; 1 = Auto, 0 = Manual
zs4_pi_qlrh_mode | PI mode for RH control of the latent load in ZS4; 1 = Auto, 0 = Manual
ahu1_h_sp_f | Setpoint temperature for the air leaving the heating coil in AHU1
ahu1_h_kp | Proportional gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_ki | Integral gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_kd | Derivative gain for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_ubias | Bias term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_sp_high | Upper limit on the temperature setpoint for the heating coil in AHU1
ahu1_h_sp_low | Lower limit on the temperature setpoint for the heating coil in AHU1
ahu1_h_pv_f | Actual temperature of the air leaving the heating coil in AHU1
ahu1_h_cv_v | Control signal for the heating coil in AHU1
ahu1_h_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU1
ahu1_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU1
ahu1_h_prop_term | Proportional term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_int_term | Integral term for the PI controller for the air leaving the heating coil in AHU1
ahu1_h_pi_mode | Not currently used
ahu1_h_sat_sp_mode | Not currently used
ahu1_cc_sp_f | Setpoint temperature for the air leaving the cooling coil in AHU1
ahu1_cc_kp | Proportional gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_ki | Integral gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_kd | Derivative gain for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_ubias | Bias term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_sp_high | Upper limit on the temperature setpoint for the cooling coil in AHU1
ahu1_cc_sp_low | Lower limit on the temperature setpoint for the cooling coil in AHU1
ahu1_cc_pv_f | Actual temperature of the air leaving the cooling coil in AHU1
ahu1_cc_cv_v | Control signal for the cooling coil in AHU1
ahu1_cc_error_f | Difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU1
ahu1_cc_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU1
ahu1_cc_prop_term | Proportional term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_int_term | Integral term for the PI controller for the air leaving the cooling coil in AHU1
ahu1_cc_pi_mode | PI mode for control the cooling coil in AHU1; 1 = Auto, 0 = Manual
ahu1_cc_sat_sp_mode | Mode for supply air temperature setpoint calculation for AHU1; 1 = Auto, 0 = Manual
ahu1_fan_sp_inh2o | Pressure setpoint for the supply fan in AHU1
ahu1_fan_kp | Proportional gain for the PI controller for the supply fan in AHU1
ahu1_fan_ki | Integral gain for the PI controller for the supply fan in AHU1
ahu1_fan_kd | Derivative gain for the PI controller for the supply fan in AHU1
ahu1_fan_ubias | Bias term for the PI controller for the supply fan in AHU1
ahu1_fan_sp_high | Upper limit on the pressure setpoint for the supply fan in AHU1
ahu1_fan_sp_low | Lower limit on the pressure setpoint for the supply fan in AHU1
ahu1_fan_pv_inh2o | Actual static pressure downstream of AHU1
ahu1_fan_cv_hz | Control signal for the speed of the supply fan in AHU1
ahu1_fan_error_inh2o | Difference between the actual and setpoint pressures downstream of AHU1
ahu1_fan_cum_error_inh2o | Integral error - sum of the difference between the actual and setpoint pressures downstream of AHU1
ahu1_fan_prop_term | Proportional term for the PI controller for the speed of the supply fan in AHU1
ahu1_fan_int_term | Integral term for the PI controller for the speed of the supply fan in AHU1
ahu1_fan_pi_mode | PI mode for control of the fan speed in AHU1; 1 = Auto, 0 = Manual
ahu1_fan_pr_mode | Mode for pressure reset calculation for AHU1; 1 = Auto, 0 = Manual
ahu2_h_sp_f | Setpoint temperature for the air leaving the heating coil in AHU2
ahu2_h_kp | Proportional gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_ki | Integral gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_kd | Derivative gain for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_ubias | Bias term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_sp_high | Upper limit on the temperature setpoint for the heating coil in AHU2
ahu2_h_sp_low | Lower limit on the temperature setpoint for the heating coil in AHU2
ahu2_h_pv_f | Actual temperature of the air leaving the heating coil in AHU2
ahu2_h_cv_v | Control signal for the heating coil in AHU2
ahu2_h_error_f | Difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU2
ahu2_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the heating coil in AHU2
ahu2_h_prop_term | Proportional term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_int_term | Integral term for the PI controller for the air leaving the heating coil in AHU2
ahu2_h_pi_mode | Not currently used
ahu2_h_sat_sp_mode | Not currently used
ahu2_cc_sp_f | Setpoint temperature for the air leaving the cooling coil in AHU2
ahu2_cc_kp | Proportional gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_ki | Integral gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_kd | Derivative gain for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_ubias | Bias term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_sp_high | Upper limit on the temperature setpoint for the cooling coil in AHU2
ahu2_cc_sp_low | Lower limit on the temperature setpoint for the cooling coil in AHU2
ahu2_cc_pv_f | Actual temperature of the air leaving the cooling coil in AHU2
ahu2_cc_cv_v | Control signal for the cooling coil in AHU2
ahu2_cc_error_f | Difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU2
ahu2_cc_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures of the air leaving the cooling coil in AHU2
ahu2_cc_prop_term | Proportional term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_int_term | Integral term for the PI controller for the air leaving the cooling coil in AHU2
ahu2_cc_pi_mode | PI mode for control the cooling coil in AHU2; 1 = Auto, 0 = Manual
ahu2_cc_sat_sp_mode | Mode for supply air temperature setpoint calculation for AHU1; 1 = Auto, 0 = Manual
ahu2_fan_sp_inh2o | Pressure setpoint for the supply fan in AHU2
ahu2_fan_kp | Proportional gain for the PI controller for the supply fan in AHU2
ahu2_fan_ki | Integral gain for the PI controller for the supply fan in AHU2
ahu2_fan_kd | Derivative gain for the PI controller for the supply fan in AHU2
ahu2_fan_ubias | Bias term for the PI controller for the supply fan in AHU2
ahu2_fan_sp_high | Upper limit on the pressure setpoint for the supply fan in AHU2
ahu2_fan_sp_low | Lower limit on the pressure setpoint for the supply fan in AHU2
ahu2_fan_pv_inh2o | Actual static pressure downstream of AHU2
ahu2_fan_cv_hz | Control signal for the speed of the supply fan in AHU2
ahu2_fan_error_inh2o | Difference between the actual and setpoint pressures downstream of AHU2
ahu2_fan_cum_error_inh2o | Integral error - sum of the difference between the actual and setpoint pressures downstream of AHU2
ahu2_fan_prop_term | Proportional term for the PI controller for the speed of the supply fan in AHU2
ahu2_fan_int_term | Integral term for the PI controller for the speed of the supply fan in AHU2
ahu2_fan_pi_mode | PI mode for control of the fan speed in AHU2; 1 = Auto, 0 = Manual
ahu2_fan_pr_mode | Mode for pressure reset calculation for AHU2; 1 = Auto, 0 = Manual
vav1_d_sp | Flow setpont for the PI controller for the damper in VAV1
vav1_d_kp | Proportional gain for the PI controller for the damper in VAV1
vav1_d_ki | Integral gain for the PI controller for the damper in VAV1
vav1_d_kd | Derivative gain for the PI controller for the damper in VAV1
vav1_d_ubias | Bias term for the PI controller for the damper in VAV1
vav1_d_sp_high | Upper limit on the flow setpoint for VAV1
vav1_d_sp_low | Lower limit on the flow setpoint for VAV1
vav1_d_pv | Actual airflow rate in VAV1
vav1_d_cv_output | Control signal for Damper15, the control damper, in VAV1
vav1_d_error | Difference between the actual and setpoint flows in VAV1
vav1_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV1
vav1_d_prop_term | Proportional term for the PI controller for the damper in VAV1
vav1_d_int_term | Integral term for the PI controller for the damper in VAV1
vav1_d_pi_mode | PI mode for control of the damper in VAV1; 1 = Auto, 0 = Manual
vav1_d_reset_mode | Mode for flow reset calculation for VAV1; 1 = Auto, 0 = Manual
vav1_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV1
vav1_h_kp | Proportional gain for the PI controller for the heating coil in VAV1
vav1_h_ki | Integral gain for the PI controller for the heating coil in VAV1
vav1_h_kd | Derivative gain for the PI controller for the heating coil in VAV1
vav1_h_ubias | Bias term for the PI controller for the heating coil in VAV1
vav1_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV1
vav1_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV1
vav1_h_pv_f | Actual temperature of the air after the heating coil in VAV1
vav1_h_cv_v | Control signal for the heating coil in VAV1
vav1_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV1
vav1_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV1
vav1_h_prop_term | Proportional term for the PI controller for the heating coil in VAV1
vav1_h_int_term | Integral term for the PI controller for the heating coil in VAV1
vav1_h_pi_mode | PI mode for control of the heating coil in VAV1; 1 = Auto, 0 = Manual
vav1_h_reset_mode | Mode for temperature reset calculation for VAV1; 1 = Auto, 0 = Manual
vav2_d_sp | Flow setpont for the PI controller for the damper in VAV2
vav2_d_kp | Proportional gain for the PI controller for the damper in VAV2
vav2_d_ki | Integral gain for the PI controller for the damper in VAV2
vav2_d_kd | Derivative gain for the PI controller for the damper in VAV2
vav2_d_ubias | Bias term for the PI controller for the damper in VAV2
vav2_d_sp_high | Upper limit on the flow setpoint for VAV2
vav2_d_sp_low | Lower limit on the flow setpoint for VAV2
vav2_d_pv | Actual airflow rate in VAV2
vav2_d_cv_output | Control signal for Damper16, the control damper, in VAV2
vav2_d_error | Difference between the actual and setpoint flows in VAV2
vav2_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV2
vav2_d_prop_term | Proportional term for the PI controller for the damper in VAV2
vav2_d_int_term | Integral term for the PI controller for the damper in VAV2
vav2_d_pi_mode | PI mode for control of the damper in VAV2; 1 = Auto, 0 = Manual
vav2_d_reset_mode | Mode for flow reset calculation for VAV2; 1 = Auto, 0 = Manual
vav2_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV2
vav2_h_kp | Proportional gain for the PI controller for the heating coil in VAV2
vav2_h_ki | Integral gain for the PI controller for the heating coil in VAV2
vav2_h_kd | Derivative gain for the PI controller for the heating coil in VAV2
vav2_h_ubias | Bias term for the PI controller for the heating coil in VAV2
vav2_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV2
vav2_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV2
vav2_h_pv_f | Actual temperature of the air after the heating coil in VAV2
vav2_h_cv_v | Control signal for the heating coil in VAV2
vav2_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV2
vav2_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV2
vav2_h_prop_term | Proportional term for the PI controller for the heating coil in VAV2
vav2_h_int_term | Integral term for the PI controller for the heating coil in VAV2
vav2_h_pi_mode | PI mode for control of the heating coil in VAV2; 1 = Auto, 0 = Manual
vav2_h_reset_mode | Mode for temperature reset calculation for VAV2; 1 = Auto, 0 = Manual
vav3_d_sp | Flow setpont for the PI controller for the damper in VAV3
vav3_d_kp | Proportional gain for the PI controller for the damper in VAV3
vav3_d_ki | Integral gain for the PI controller for the damper in VAV3
vav3_d_kd | Derivative gain for the PI controller for the damper in VAV3
vav3_d_ubias | Bias term for the PI controller for the damper in VAV3
vav3_d_sp_high | Upper limit on the flow setpoint for VAV3
vav3_d_sp_low | Lower limit on the flow setpoint for VAV3
vav3_d_pv | Actual airflow rate in VAV3
vav3_d_cv_output | Control signal for Damper17, the control damper, in VAV3
vav3_d_error | Difference between the actual and setpoint flows in VAV3
vav3_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV3
vav3_d_prop_term | Proportional term for the PI controller for the damper in VAV3
vav3_d_int_term | Integral term for the PI controller for the damper in VAV3
vav3_d_pi_mode | PI mode for control of the damper in VAV3; 1 = Auto, 0 = Manual
vav3_d_reset_mode | Mode for flow reset calculation for VAV3; 1 = Auto, 0 = Manual
vav3_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV3
vav3_h_kp | Proportional gain for the PI controller for the heating coil in VAV3
vav3_h_ki | Integral gain for the PI controller for the heating coil in VAV3
vav3_h_kd | Derivative gain for the PI controller for the heating coil in VAV3
vav3_h_ubias | Bias term for the PI controller for the heating coil in VAV3
vav3_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV3
vav3_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV3
vav3_h_pv_f | Actual temperature of the air after the heating coil in VAV3
vav3_h_cv_v | Control signal for the heating coil in VAV3
vav3_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV3
vav3_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV3
vav3_h_prop_term | Proportional term for the PI controller for the heating coil in VAV3
vav3_h_int_term | Integral term for the PI controller for the heating coil in VAV3
vav3_h_pi_mode | PI mode for control of the heating coil in VAV3; 1 = Auto, 0 = Manual
vav3_h_reset_mode | Mode for temperature reset calculation for VAV3; 1 = Auto, 0 = Manual
vav4_d_sp | Flow setpont for the PI controller for the damper in VAV4
vav4_d_kp | Proportional gain for the PI controller for the damper in VAV4
vav4_d_ki | Integral gain for the PI controller for the damper in VAV4
vav4_d_kd | Derivative gain for the PI controller for the damper in VAV4
vav4_d_ubias | Bias term for the PI controller for the damper in VAV4
vav4_d_sp_high | Upper limit on the flow setpoint for VAV4
vav4_d_sp_low | Lower limit on the flow setpoint for VAV4
vav4_d_pv | Actual airflow rate in VAV4
vav4_d_cv_output | Control signal for Damper18, the control damper, in VAV4
vav4_d_error | Difference between the actual and setpoint flows in VAV4
vav4_d_cum_error | Integral error - sum of the difference between the actual and setpoint flows in VAV4
vav4_d_prop_term | Proportional term for the PI controller for the damper in VAV4
vav4_d_int_term | Integral term for the PI controller for the damper in VAV4
vav4_d_pi_mode | PI mode for control of the damper in VAV4; 1 = Auto, 0 = Manual
vav4_d_reset_mode | Mode for flow reset calculation for VAV4; 1 = Auto, 0 = Manual
vav4_h_sp_f | Temperature setpont for the PI controller for the heating coil in VAV4
vav4_h_kp | Proportional gain for the PI controller for the heating coil in VAV4
vav4_h_ki | Integral gain for the PI controller for the heating coil in VAV4
vav4_h_kd | Derivative gain for the PI controller for the heating coil in VAV4
vav4_h_ubias | Bias term for the PI controller for the heating coil in VAV4
vav4_h_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV4
vav4_h_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV4
vav4_h_pv_f | Actual temperature of the air after the heating coil in VAV4
vav4_h_cv_v | Control signal for the heating coil in VAV4
vav4_h_error_f | Difference between the actual and setpoint temperatures after the heating coil in VAV4
vav4_h_cum_error_f | Integral error - sum of the difference between the actual and setpoint temperatures after the heating coil in VAV4
vav4_h_prop_term | Proportional term for the PI controller for the heating coil in VAV4
vav4_h_int_term | Integral term for the PI controller for the heating coil in VAV4
vav4_h_pi_mode | PI mode for control of the heating coil in VAV4; 1 = Auto, 0 = Manual
vav4_h_reset_mode | Mode for temperature reset calculation for VAV4; 1 = Auto, 0 = Manual
ahu1_sa_sp_per | Setpoint for the percent outdoor air for AHU1
ahu1_sa_kp | Proportional gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_ki | Integral gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_kd | Derivative gain for the PI controller for the percent outdoor air for AHU1
ahu1_sa_ubias | Bias term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_sp_high | Upper limit on the percent outdoor air for AHU1
ahu1_sa_sp_low | Lower limit on the percent outdoor air for AHU1
ahu1_sa_pv_per | Actual percent outdoor air for AHU1
ahu1_sa_cv_v | Control signal for Damper6, the supply air damper, for AHU1
ahu1_sa_error_per | Difference between the actual and setpoint percent outdoor air for AHU1
ahu1_sa_cum_error_per | Integral error - sum of the difference between the actual and setpoint percent outdoor air for AHU1
ahu1_sa_prop_term | Proportional term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_int_term | Integral term for the PI controller for the percent outdoor air for AHU1
ahu1_sa_pi_mode | PI mode for the emulated outdoor air damper in AHU1; 1 = Auto, 0 = Manual
ahu2_sa_sp_per | Setpoint for the percent outdoor air for AHU2
ahu2_sa_kp | Proportional gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_ki | Integral gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_kd | Derivative gain for the PI controller for the percent outdoor air for AHU2
ahu2_sa_ubias | Bias term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_sp_high | Upper limit on the percent outdoor air for AHU2
ahu2_sa_sp_low | Lower limit on the percent outdoor air for AHU2
ahu2_sa_pv_per | Actual percent outdoor air for AHU2
ahu2_sa_cv_v | Control signal for Damper7, the supply air damper, for AHU2
ahu2_sa_error_per | Difference between the actual and setpoint percent outdoor air for AHU2
ahu2_sa_cum_error_per | Integral error - sum of the difference between the actual and setpoint percent outdoor air for AHU2
ahu2_sa_prop_term | Proportional term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_int_term | Integral term for the PI controller for the percent outdoor air for AHU2
ahu2_sa_pi_mode | PI mode for the emulated outdoor air damper in AHU2; 1 = Auto, 0 = Manual
ahu1_n_pr | Number of timesteps between setpoint changes for pressure reset for the supply fan in AHU1
ahu1_thresh_high_pr | Threshold on the VAV dampers that indicates more cooling is needed (the positions of either damper is above this threshold)
ahu1_thresh_low_pr | Threshold on the VAV dampers that indicates less cooling is needed (the positions of both dampers are below this threshold)
ahu1_delta_pr | Magnitude of the change of the pressure setpoint for the supply fan in AHU1
ahu2_n_pr | Number of timesteps between setpoint changes for pressure reset for the supply fan in AHU2
ahu2_thresh_high_pr | Threshold on the VAV dampers that indicates more cooling is needed (the positions of either damper is above this threshold)
ahu2_thresh_low_pr | Threshold on the VAV dampers that indicates less cooling is needed (the positions of both dampers are below this threshold)
ahu2_delta_pr | Magnitude of the change of the pressure setpoint for the supply fan in AHU2
vav1_fr_sp | Temperature setpont for the air leaving ZS1
vav1_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV1
vav1_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV1
vav1_fr_pv | Actual temperature leaving ZS1
vav1_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV1
vav1_fr_error | Difference between the actual and setpoint temperatures for ZS1
vav1_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
vav1_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV1
vav1_fr_pi_mode | PI mode for calculation of the airflow rate in VAV1; 1 = Auto, 0 = Manual
vav1_fr_reset_mode | Mode for the flow reset controller in VAV1; 1 = Auto, 0 = Manual
vav2_fr_sp | Temperature setpont for the air leaving ZS2
vav2_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV2
vav2_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV2
vav2_fr_pv | Actual temperature leaving ZS2
vav2_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV2
vav2_fr_error | Difference between the actual and setpoint temperatures for ZS2
vav2_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
vav2_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV2
vav2_fr_pi_mode | PI mode for calculation of the airflow rate in VAV2; 1 = Auto, 0 = Manual
vav2_fr_reset_mode | Mode for the flow reset controller in VAV2; 1 = Auto, 0 = Manual
vav3_fr_sp | Temperature setpont for the air leaving ZS3
vav3_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV3
vav3_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV3
vav3_fr_pv | Actual temperature leaving ZS3
vav3_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV3
vav3_fr_error | Difference between the actual and setpoint temperatures for ZS3
vav3_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
vav3_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV3
vav3_fr_pi_mode | PI mode for calculation of the airflow rate in VAV3; 1 = Auto, 0 = Manual
vav3_fr_reset_mode | Mode for the flow reset controller in VAV3; 1 = Auto, 0 = Manual
vav4_fr_sp | Temperature setpont for the air leaving ZS4
vav4_fr_kp | Proportional gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_ki | Integral gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_kd | Derivative gain for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_ubias | Bias term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_sp_high | Upper limit on the flow setpoint for the damper in VAV4
vav4_fr_sp_low | Lower limit on the flow setpoint for the damper in VAV4
vav4_fr_pv | Actual temperature leaving ZS4
vav4_fr_cv_output | Flow setpoint calculated by the PI controller for the damper in VAV4
vav4_fr_error | Difference between the actual and setpoint temperatures for ZS4
vav4_fr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
vav4_fr_prop_term | Proportional term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_int_term | Integral term for the PI controller for the flow setpoint calculation for the damper in VAV4
vav4_fr_pi_mode | PI mode for calculation of the airflow rate in VAV4; 1 = Auto, 0 = Manual
vav4_fr_reset_mode | Mode for the flow reset controller in VAV4; 1 = Auto, 0 = Manual
vav1_tr_sp | Temperature setpont for the air leaving ZS1
vav1_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV1
vav1_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV1
vav1_tr_pv | Actual temperature leaving ZS1
vav1_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV1
vav1_tr_error | Difference between the actual and setpoint temperatures for ZS1
vav1_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
vav1_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV1
vav1_tr_pi_mode | PI mode for calculation of the reheat temperature in VAV1; 1 = Auto, 0 = Manual
vav1_tr_reset_mode | Mode for the temperature reset controller in VAV1; 1 = Auto, 0 = Manual
vav2_tr_sp | Temperature setpont for the air leaving ZS2
vav2_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV2
vav2_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV2
vav2_tr_pv | Actual temperature leaving ZS2
vav2_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV2
vav2_tr_error | Difference between the actual and setpoint temperatures for ZS2
vav2_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
vav2_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV2
vav2_tr_pi_mode | PI mode for calculation of the reheat temperature in VAV2; 1 = Auto, 0 = Manual
vav2_tr_reset_mode | Mode for the temperature reset controller in VAV2; 1 = Auto, 0 = Manual
vav3_tr_sp | Temperature setpont for the air leaving ZS3
vav3_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV3
vav3_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV3
vav3_tr_pv | Actual temperature leaving ZS3
vav3_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV3
vav3_tr_error | Difference between the actual and setpoint temperatures for ZS3
vav3_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
vav3_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV3
vav3_tr_pi_mode | PI mode for calculation of the reheat temperature in VAV3; 1 = Auto, 0 = Manual
vav3_tr_reset_mode | Mode for the temperature reset controller in VAV3; 1 = Auto, 0 = Manual
vav4_tr_sp | Temperature setpont for the air leaving ZS4
vav4_tr_kp | Proportional gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_ki | Integral gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_kd | Derivative gain for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_ubias | Bias term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_sp_high | Upper limit on the temperature setpoint for the heating coil in VAV4
vav4_tr_sp_low | Lower limit on the temperature setpoint for the heating coil in VAV4
vav4_tr_pv | Actual temperature leaving ZS4
vav4_tr_cv_output | Temperature setpoint calculated by the PI controller for the heating coil in VAV4
vav4_tr_error | Difference between the actual and setpoint temperatures for ZS4
vav4_tr_cum_error | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
vav4_tr_prop_term | Proportional term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_int_term | Integral term for the PI controller for the temperature setpoint calculation for the heating coil in VAV4
vav4_tr_pi_mode | PI mode for calculation of the reheat temperature in VAV4; 1 = Auto, 0 = Manual
vav4_tr_reset_mode | Mode for the temperature reset controller in VAV4; 1 = Auto, 0 = Manual
zs1_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS1
zs1_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs1_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV1
zs2_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS2
zs2_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs2_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV2
zs4_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS4
zs4_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs4_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV4
zs3_rl_iterm | Integral term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_pterm | Proportional term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_ierror | Integral error - sum of the difference between the actual and setpoint temperatures for ZS3
zs3_rl_e | Exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV3
zs3_rl_e_amp | Amplitude of the exploratory term for the RL controller for the temperature setpoint for the heating coil in VAV3
comms_timestep | Timestep when communicating with the DOE project simulation
comms_doe_mode | Mode of the DOE project; 1 = Communicating with DOE project simulation, 0 = Not communicating with DOE project simulation
airhl_on | Air system mode; 1 = Auto, 0 = Manual
airhl_start | Air system in start mode; 1 = True, 0 = False
airhl_backend | Air system controlled from the backend; 1 = True, 0 = False
airhl_occupancy | Occupied mode when the air system mode is in Auto; 1 = occupied, 0 = unoccupied
airhl_zs | ZS mode when air system mode is auto; 1 = On, 0 = Off
airhl_flowReset | VAV flow reset mode when air system mode is auto; 1 = On, 0 = Off
airhl_ccValve | AHU cooling coil valve mode when air system mode is auto; 1 = On, 0 = Off
airhl_sat | AHU supply air temperature mode when air system mode is auto; 1 = On, 0 = Off
waterhl_on | Water system mode; 1 = Auto, 0 = Manual
waterhl_backend | Water system controlled from the backend; 1 = True, 0 = False
ahu1_fr_sp_w | Setpoint for AHU1 fan when using frequency regulation; Watt difference from baseline power
ahu1_fr_kp | Proportional gain for the PI controller for the frequency regulation calculation for the AHU1 fan
ahu1_fr_ki | Integral gain for the PI controller for the frequency regulation calculation for the AHU1 fan
ahu1_fr_kd | Derivative gain for the PI controller for the frequency regulation calculation for the AHU1 fan
ahu1_fr_ubias | Bias term for the PI controller for the frequency regulation calculation for the AHU1 fan
ahu1_fr_sp_high | Upper limit on the power difference from baseline setpoint for the fan power in AHU1
ahu1_fr_sp_low | Lower limit on the power difference from baseline setpoint for the fan power in AHU1
ahu1_fr_pv_w | Actual fan power difference from baseline for AHU1 fan in frequency regulation
ahu1_fr_cv_inh2o | Pressure offset setpoint calculated by the PI controller for the fan power difference from baseline for the AHU1 fan in frequency regulation
ahu1_fr_error_w | Difference between the actual and setpoint fan power difference from baseline for AHU1
ahu1_fr_cum_error_w | Integral error - sum of the difference between the actual and setpoint fan power difference from baseline for AHU1
ahu1_fr_prop_term | Proportional term for the PI controller for the fan power difference from baseline for AHU1
ahu1_fr_int_term | Integral term for the PI controller for the fan power difference from baseline for AHU1
ahu1_fr_pi_mode | PI mode for calculation of the pressure offset for frequency regulation for AHU1
ahu1_fr_deriv_term | Derivative term for the PI controller for the fan power difference from baseline for AHU1
ahu1_fr_erate | Derivative error rate for the PI controller for the fan power difference from baseline for AHU1
ahu1_fr_regA | RegA signal for frequency regulation for AHU1
ahu1_fr_basePower | AHU1 baseline fan power for frequency regulation
ahu1_fr_dPower | Multiplier for the regA signal to generate the fan power difference for AHU1
ahu1_fr_frMode | Frequency regulation mode - typically 1 between timesteps 480 and 520
ahu2_fr_sp_w | Setpoint for AHU2 fan when using frequency regulation; Watt difference from baseline power
ahu2_fr_kp | Proportional gain for the PI controller for the frequency regulation calculation for the AHU2 fan
ahu2_fr_ki | Integral gain for the PI controller for the frequency regulation calculation for the AHU2 fan
ahu2_fr_kd | Derivative gain for the PI controller for the frequency regulation calculation for the AHU2 fan
ahu2_fr_ubias | Bias term for the PI controller for the frequency regulation calculation for the AHU2 fan
ahu2_fr_sp_high | Upper limit on the power difference from baseline setpoint for the fan power in AHU2
ahu2_fr_sp_low | Lower limit on the power difference from baseline setpoint for the fan power in AHU2
ahu2_fr_pv_w | Actual fan power difference from baseline for AHU2 fan in frequency regulation
ahu2_fr_cv_inh2o | Pressure offset setpoint calculated by the PI controller for the fan power difference from baseline for the AHU2 fan in frequency regulation
ahu2_fr_error_w | Difference between the actual and setpoint fan power difference from baseline for AHU2
ahu2_fr_cum_error_w | Integral error - sum of the difference between the actual and setpoint fan power difference from baseline for AHU2
ahu2_fr_prop_term | Proportional term for the PI controller for the fan power difference from baseline for AHU2
ahu2_fr_int_term | Integral term for the PI controller for the fan power difference from baseline for AHU2
ahu2_fr_pi_mode | PI mode for calculation of the pressure offset for frequency regulation for AHU2
ahu2_fr_deriv_term | Derivative term for the PI controller for the fan power difference from baseline for AHU2
ahu2_fr_erate | Derivative error rate for the PI controller for the fan power difference from baseline for AHU2
ahu2_fr_regA | RegA signal for frequency regulation for AHU2
ahu2_fr_basePower | AHU2 baseline fan power for frequency regulation
ahu2_fr_dPower | Multiplier for the regA signal to generate the fan power difference for AHU2
ahu2_fr_frMode | Frequency regulation mode - typically 1 between timesteps 480 and 520